## Specification solar-cabinets BF
Position | Item | Technical Requirements A comprehensive technical quotation in PDF format, including all technical data sheets, must be submitted as ONE SINGLE PDF file. | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns A-C, please indicate "Yes". Otherwise, describe your special features in this column. Conformity of individual components with the technical specifications listed below must be proven with technical data sheets in PDF format. In addition to the information provided in this form, a comprehensive technical quotation in PDF format, including all technical data sheets, must be submitted as one single PDF file
1 | General Requirements
1.1 | Pre-wired off-grid solar power cabinet solution | The proposed solution must be pre-configured, pre-assembled, standardised, standalone off-grid solar power system with a solar field capacity of min. 10 kWc, an inverter capacity of min. 10 kVA, a storage capacity of min. 30 kWh, single phase 230V The entire installation, with the exception of the solar modules and cooling / air condition, must be carried out within a closed and ventilated cabinet, as a turnkey, plug-and-play solution. Main components such as inverters, and batteries, controlers, etc. have to be completly prewired and pre-installed. For security reasons during transport, batteries can be installed on-site, an easy rack-mounting is required, also wiring of battery modules must be carried out in such a way as to minimise the risk of incorrect connection. The PV module structures must be made of stainless steel or aluminum incorporating anti-theft bolts. Ground mounted structure is required with a tilt of 10° to 25°. - eight cabinets inc. solar field and mounting structure are necessary (= 8 standalone off-grid solar power system) - External dimensions of cabinet : max 750mm length x 60mm width x 1850mm height - The weight per cabinbet must be limited so that two persons can carry one cabinet (without mounted battery modules) - Including temperature controlled automatic cooling-system (for a room size of approx. 16 square metres)
1.2 | Power grid | The s off-grid solar power cabinet solution must allow the supply of electrical loads at a voltage of 230 VAC (1W+1N+1PE; 1 phase, 1 neutral conductor, 1 earth conductor)
1.3 | Basic design principles | The components of the proposed container solution must be fully functional and compatible with each other. All components and parts not explicitly mentioned in this document, but necessary to ensure a professional installation and flawless operation, must be provided by the bidder (except for parts explicitly excluded from the tender).
1.4 | The main components of the solar container solution | Cabinet, PV Modules, PV Module Structure, Solar Charge Controller, Inverter or Inverter integrating the charge controller, Batteries, Monitoring System and electrical protection equipment.
1.5 | Standards and norms | The standards mentioned in this specification may also be offered by equivalent standards as long as they cover the same requirements.
2 | Photovolatic Modules
2.1 | Power of the solar field | min. 10 kWc
2.2 | Technical data of the module | PV modules with crystalline technology. Output per module min. 450 W, tolerance 0 - 5%. Certification for wind load in Sahel region. Solar cells are embedded in an EVA (ethylene vinyl acetate) layer, anti-reflective coating, front cover made of specially tempered, highly transparent glass. Framed with aluminium profile (anodised).
2.3 | Product Certification | The module complies with the following certifications: - IEC 61 215 : Terrestrial photovoltaic (PV) modules - Type qualification and type approval. - IEC 61 730 : Photovoltaic (PV) modules - safety qualification The tests are carried out by recognised testing laboratories according to ISO/IEC 17025. The manufacturer of the solar modules can prove by a suitable certificate that a permanent quality control and assurance of the production processes takes place in his factory. It must be proven that the standards according to IEC 61215 and IEC 61730 are also adhered to in ongoing production. The certificate itself is issued by an accredited testing institute. The normative requirements IEC 60891 ; IEC 60904 ; IEC 61345 ; IEC 61701; IEC 61721; EN 50380 are fulfilled. CE Declaration of Conformity by the manufacturer is available. A confirmation by a conformity assessment body according to ISO/IEC 17021 is available. CE marking of the solar modules is available. The solar modules are marked accordingly. Weatherproof junction box on the back of the module. The junction box must comply with at least IP 65 and the DIN VDE 0126-5 standard. The cabling between the modules with connectors complies with the EN 50521 standard.
2.4 | Power and Product Guarantee | ≤1% Degradation in the first year, ≤0.4% Annual degradation over 30 years Product guarantee for at least 10 years
2.5 | Please specify: | Brand name, model, type
Area of the cells (LxW) in mm
Dimensions of the module (LxWxD) in mm
Weight of module in kg
Maximum power (Pmax) W
Maximum voltage ( Vmax) V
Maximum current ( Ipmax) A
Maximum reverse current IR [A]
Short-circuit current (Isc) A
Open circuit voltage ( Voc) V
Temperature coefficient for current A/°C
Temperature coefficient for voltage V/°C
Temperature coefficient for power %/°C
Nominal cell operating temperature ( NOCT)
Maximum system voltage ( Vsmax )
Operating temperature ( Min- Max ) °C
Ambient temperature ( Min - Max ) °C
Current-voltage characteristics at 25°C and other temperatures and irradiation
2.6 | Please enclose with quotation: | Data sheet
Test certificates according to IEC 61215 and IEC 61730
Certificates according to ISO/IEC 17025
Accreditation of the test centre/institute or test centres (IEC 61215, IEC 61730 and ISO/IEC 17025) according to EN 45011 - 45013
CE declaration of conformity of the manufacturer
Confirmation that upon delivery of the modules, the flasher protocols showing the rated power of all delivered modules are presented and handed over.
Declaration or explicit confirmation regarding the replacement of the modules according to item 2.3.
Explanations on packaging and handling of the solar modules with reference to IEC 62759-1
3 | Structure
3.1 | Structure | The substructure made of aluminium or stainless steel must support the modules and withstand the local weather conditions in Burkina Faso, region of Fada N'Gourmai. It must be sufficiently protected against corrosion. The structure is mounted on the ground Inclination angle of the PV module field adjustable between 10 - 25° relative to the horizontal plane. Special anti-theft bolts and nuts to match the modules. Lightning protection and earthing
3.2 | Ground conditions | From laterite soil to sandy subsoil
3.3 | Manufacturer Warranty | min. 10 years
3.4 | Please specify: | Brand name, model, type
Data sheet
Detailed description of the anti-theft screws and nuts
Technical description of the substructure
Description of the lightning protection
3.5 | In case of order, to be provided before delivery: | Sectional drawings of the profiles and elevations
Detailed drawings of fixings (interfaces, connections)
Assembly instructions in French
4 | Inverter
4.1 | PowerControl & PowerAssist | Yes
4.2 | Total inverter capacity | 10 kVA
4.4 | System output voltage | 230 VAC (1W+1N+1PE)
4.5 | Unit capacity of inverters | 1x10kVA
4.6 | Inverter unit | The following functions are fulfilled: - enables supply of consumers with 230 V AC - charges the battery with an integrated MPPT charge controller [Max. battery charge current : 70A]. - simultaneously allows connection to a generator or power grid - U-I generator diagnosis - Protective conductor monitoring - Max apparent feed-in power : 10 000 VA
4.7 | Capacity unit | Continuous power min. 10 000 VA System voltage 48 V Output voltage 230 V AC +/- 5% Output frequency 50/60 Hz Pure sine wave voltage Integrated MPP tracker, multi-stage charging technology Adjustable end-of-charge voltages Adjusted to the interconnecting solar modules from position 2 and, if applicable, known consumer devices.
4.8 | Standards | Safety : EN-IEC 60335-1, EN-IEC 60335-2-29, EN-IEC 62109-1, EN-IEC 62109-2, AS 62477.1:2016, AS/NZS.2:2020 Inc A1
4.9 |  | Emission, Immunity : EN 55014-1, EN 55014-2 EN-IEC 61000-3-2, EN-IEC 61000-3-3, IEC 61000-6-1, IEC 61000-6-2, IEC 61000-6-3
4.10 | Quantity of inverter/charger units | 1
5 | SmartSolar Charge Controller with VE.Can interface
5.1 | SmartSolar Charge Controller | Charge controller with MPPT technology. Maximum self-consumption 1 W. Complies with EN 62109-1. Electrical efficiency >90% (at 5 to 120% nominal power). Possibility to connect a remote control / remote monitoring is available Protection category : IP43 (electronic components), IP22 (connection area) Battery voltage : 12/24/48 V Auto Select Rated charge current : Min 100A Operating temperature : -30 to +60 °C (full rated output up to 40 °C) Safety : EN/IEC 62109-1, UL 1741, CSA C22.2 VE.Can interface It is recommended to consider inverters that incorporate charge controllers, see 4.6
5.2 | Certifications and standards | It must comply with the following standards: EN-IEC 60335-1, EN-IEC 60335-2-29, EN-IEC 62109-1, EN 55014-1, EN 55014-2, EN-IEC 61000-3-2, IEC 61000-6-1, IEC 61000-6-2, IEC 61000-6-3. Manufactured according to ISO 9001 and ISO 14001. CE compliant
6 | Monitoring system
6.1 | Monitoring system | User-friendly interface with intuitive web platform or mobile app. Data visualization via graphs, charts, and tables. Track daily, monthly, yearly, and total energy generation (kWh). Display real-time operating parameters (power, voltage, etc.). Access to historical data and trends. Configurable user access levels for owners, technicians, and maintenance staff. Via GSM connection or a local network with LAN or WiFi The monitoring system must enable fleet management (i.e. monitoring of multiple systems) and allow comparison of system performance / remote support
6.2 | Quantity of Monitoring system | 1
7 | Battery
7.1 | Lithium-ion battery | More than 6,000 cycles at 25°C / Nominal capacity : Min 5 000 Ah Service life according to EUROBAT min. 12 years at 20°C Standards and regulations for installation: DIN EN 50272-2 (safety regulations for battery rooms) Reference standards and certificats (mandatory): CE, UN 38.3, IEC 62619 and IEC 62477. Further reference standards: IEC 63056, IEC 61000-6-2, IEC 61000-6-3. The battery must be supplied with its rack certified by the manufacturer. Proof of quality assurance system according to ISO 9001 / ISO 14001 ISO 45001 occupational health and safety or equivalent certification Fully insulated, corrosion-free lead terminal All pole penetrations must ensure complete electrolyte and gas tightness even when positive plate is growing Fully insulated copper connectors and screw heads Interconnection lead poles with torque 20 - 22 Nm Environmentally friendly, min. 98 % recyclable Energy efficiency > 80% Ampere-hour efficiency > 90% Self-discharge less than 2-3%/month at 20°C Operating temperature charging/discharging until min. 50°C No memory effect Sufficiently large containers for electrolyte circulation Each battery is labelled with at least the following data: Manufacturer, type, model number, nominal voltage in V, nominal capacity in Ah, month and year of commissioning. Each cell must have a factory serial number
7.2 | Battery unit quantity | 6
8 | Cable
8.1 | Solar cables | 1x [10] mm² copper cable with double insulation for up to 1000V, type C2 (high flame resistance), AN3 (high UV resistance) Maximum permissible conductor temperature at least 90°C in continuous use. The standard EN 50618 is fulfilled. Please calculate required diameters accroding to cable lengths and for a fully functional system operation. Solar DC wiring must be carried out in accordance with IEC 62930:2017. The minimum distance between the solar field and the planned location for the installation of the cabinet is 40m
8.2 | DC Cables | [Aluminium / Copper] Please calculate cable lengths and diameters for a fully functional system operation. Solar DC wiring must be carried out in accordance with IEC 62930:2017. Note: The wiring must be done at the factory
8.3 | AC Cables | [Aluminium / Copper] Please calculate cable lengths and diameters for a fully functional system operation. The AC wiring must be carried out in accordance with NFC 15-100 and according to the technical specifications for the building. Note: The wiring must be done at the factory
8.4 | Empty conduits | PE cable conduits for burial, double wall (corrugated outside, smooth inside according to standard NF EN 50086-2-4)
8.5 | Cable ties | UV-resistant cable ties in all necessary sizes and quantities.
8.6 | Accessories | All accessories for proper fastening of the cables under the modules for the entire installation.
9 | Others
9.1 | Ventilation / cooling of cabinet | An automatic air extractors equipped with air filters will be necessary to ensure the control and regulation of the internal temperature of the cabinet. In addition, it should be possible to connect an air-conditioning system which switches on and off automatically via temperature sensors when temperatures exceed the normal operating range.
9.2 | Connection terminal cabinet solar systems with main electric system/infrastructure | The connection of the terminals of the cabinet solar systems to the main electrical installation system of infrastructures such as deep-well pumps, health centres, school buildings, etc. will be done by AC cable (cross-section and calculation note to be provided by each supplier) in buried mode over a minimum distance to be considered of 20 m
9.3 | Connection terminal for interconnection of PV modules | The interconnection of the PV modules and the DC cables of the 'PV field - Cabinet inverter' link will be done through MC4 solar connectors.
9.4 | Connection of inverter/Charger units | The inverter/charger units must be connected to each other by RJ45 cables and powered by the batteries, thus forming a single one-phase storage system.
10 | Documentation
10.1 | The following documentation, in French, must be supplied in electronic form for all components of the system after the order has been placed: | Assembly instructions for the entire system. Overview for an installer on site, showing which components are connected to each other and how. This overview also refers to the corresponding installation instructions and assembly instructions for the individual components.
10.2 |  | Circuit document
10.3 |  | Description of the components
10.4 |  | Wiring diagrams
10.5 |  | Assembly instructions, installation instructions
10.6 |  | Commissioning instructions
10.7 |  | Operating instructions
10.8 |  | Maintenance instructions
10.9 |  | Error analysis and troubleshooting suggestions in the event of a malfunction
11 | Spare parts / Tool kit
11.1 | Solar modules | min. 2 PV modules, per system
11.2 | Components and equipment | Kit of spare parts, like screws, clips, etc.
11.3 |  | Please specify:
11.4 | Tool kit | Each system must be supplied with a complete set of tools (= 6 kits) required to carry out on-site commissioning (e.g. ratchet set, pliers, screwdrivers, voltage tester, etc.)
11.5 |  | Please specify:
12 | Material Delivery
12.1 | Delivery | All material must be delivered DPU GIZ-Office in Ouagadougou, Burkina Faso, latest four months after order.
12.2 | Please specify: | Dimensions of standard ISO container incl. packaging for sea and truck shipment.
12a | Customs clearance (by giz)
| Customs clearance (by giz) | Customs clearance will be done by giz.
12b | Domestic Material Transport (by giz)
| Domestic Material Transport (by giz) | Domestic transport will be done by giz.
13 | Warranty
13.1 | min. 2 years | On the entire system and installation. Fully according to GIZ General Purchase Conditions (GPC) 2023. The claims arising from the product and system warranties apply in addition to the claims for defects in accordance with GIZ GPC 2023. For individual components, longer warranty periods apply if described.
13.2 | Place of validity | All guarantee and warranty conditions apply at the locations of the installed PV-Systems. Even if the material was handed over at other locations. This applies only insofar as the locations of the installed systems are accessible. Otherwise, spare parts must be delivered to the nearest GIZ office and technical support must be provided remotely.
13.3 | Guarantee assignment declarations | All warranties must be assigned to GIZ and project partners by declaration. This declaration must be signed and stamped by each manufacturer.
14 | Training (optional)
14.1 | Remote traininig | Min. 2 days The manufacturer must provide a training for instruction on installation and operation for at least one expert designated by GIZ.