# Technical Specification

Lot 1 is for 5 m3/h devices with 20 units, Lot 2 is nearly identical but for 10 m3/h devices with 10 units.

This tender is only for delivery and online training – no physical service at the delivery point is requested while the beneficiaries will be selected at a later stage.

## 1.1. Lot 1: Reverse Osmosis (RO) Water Treatment Unit, 5 m3/h permeate capacity (skid-mounted, complete system) - equipment

GENERAL

Skid-mounted, fully automated, factory pre-assembled and pre-tested reverse osmosis (RO) water treatment unit for district heating (DH) make-up water treatment

Suitable for indoor installation and continuous operation at DH utility sites in Ukraine

Nominal permeate capacity: 5 m3/h at the reference feed water quality stated below

Recovery rate: minimum 75% (an outcome of the bidder's project-specific design calculation for the stated feed water quality; see MEMBRANE BLOCK and HIGH-PRESSURE PUMP below - not a fixed band)

Bidder shall submit a project-specific membrane design/projection report (e.g. ROSA, IMSDesign or equivalent) confirming the offered configuration meets this capacity at the stated feed water quality

The report shall contain at least: raw water quality and design temperature; membrane type and manufacturer; number of pressure vessels and membrane elements; membrane area and array; design flux; permeate and concentrate flow; recovery; operating pressure; permeate quality and salt rejection; expected ion concentrations and saturation indices in the concentrate (CaCO3, CaSO4, BaSO4, SrSO4, SiO2); required antiscalant dosing; specific energy consumption and its basis of calculation. It shall be based on the worst-case raw water quality stated above; the bidder shall name any further water analyses required for the final membrane design

FEED WATER DESIGN BASIS (worst-case Ukrainian DH raw water)

Total hardness: up to 20 mg-eq/dm3

Total dissolved solids (TDS): up to 1,500 mg/dm3

Iron content: up to 1.2 mg/dm3

The bidder shall state the further feed water parameters assumed in the design (temperature range, pH, alkalinity, calcium, magnesium, sulphate, silica, chloride, sodium, manganese, turbidity, SDI); site-specific raw water analyses shall be checked before commissioning

The bidder shall state the maximum allowable RO-inlet values required by the membrane manufacturer (total and dissolved iron, manganese, SDI, turbidity, residual oxidants); meeting these values by upstream treatment (e.g. iron removal) is the responsibility of the DH utility

PRE-FILTRATION

5-micron sediment cartridge filters, heavy-duty, quick-replace multi-cartridge housing, sized for full design flow

ANTISCALANT DOSING

Digital diaphragm metering pump with proportional (flow-paced) dosing control

Dedicated chemical day-tank with low-level alarm

Antiscalant formulation compatible with the stated hardness/iron/TDS

HIGH-PRESSURE PUMP

Multistage pump, stainless steel wetted parts (min. AISI 316), with Variable Frequency Drive (VFD)

Operating pressure is an outcome of the bidder's project-specific membrane design calculation for the stated feed water quality, the specified flux limit and the selected recovery (indicative reference range for this water quality: 14-18 bar; not a fixed requirement)

Specific energy consumption: to be calculated by the bidder and stated as a guaranteed value (kWh/m3 of permeate) at clean membranes and design temperature, measured at the skid boundary (high-pressure pump plus all auxiliary/dosing drives mounted on the skid; excludes external balance-of-plant equipment such as buffer-tank transfer pumps); to be provided together with the supporting pump curve and system energy balance specific to the offered 5 m3/h capacity, and documented in the factory test report (see FACTORY ACCEPTANCE TEST below)

MEMBRANE BLOCK

High-rejection, fouling-resistant polyamide thin-film composite (TFC) spiral-wound elements; commercially available and replaceable from more than one manufacturer (no proprietary/non-standard format); element diameter (4-inch or 8-inch) to be selected by the bidder as appropriate for the offered capacity and array design, and justified in the design calculation

Minimum nominal salt (NaCl) rejection per element: 99.5%, per manufacturer's standard test conditions

Maximum average design permeate flux: 18 L/(m2*h), appropriate for iron-bearing feed water; bidder to state the number of elements/pressure vessels and the resulting design flux in the technical offer

Recovery: minimum 75% (bidder may propose a higher design recovery where justified by the feed water quality, flux limit and element selection)

Bidder to state expected element life under the stated feed water (indicative range: 2-3 years, versus a 5-6 year nominal design life, due to the aggressive raw water)

pH CORRECTION (CO2 NEUTRALIZATION)

Dedicated NaOH dosing pump and day-tank on the permeate line

Function: neutralize free CO2 and raise permeate pH from approx. 5.0-5.3 to 8.5-9.5

Automatic, pH-controlled proportional dosing, interlocked with an online permeate pH sensor

Residual free CO2 is removed in the utility's existing thermal deaeration (not part of the supply); the bidder shall state the expected free CO2 concentration in the permeate and the resulting NaOH consumption

CLEAN-IN-PLACE (CIP) SYSTEM

Fully integrated CIP station: cleaning tank, circulation pump, cartridge pre-filter, valves and piping for both low-pH (acid) and high-pH (alkaline) cleaning cycles

Cleaning cycle sequencing via the PLC (automatic or semi-automatic)

INSTRUMENTATION & CONTROL (PLC)

PLC controller with colour touchscreen HMI

Continuous online monitoring and PLC logging of: electrical conductivity (EC) of raw water and permeate; temperature; pH of raw water and permeate; permeate and concentrate flow rates

4-20 mA and/or dry-contact outputs for remote monitoring/SCADA integration

Automatic low-pressure, high-pressure and dry-run protection interlocks on the high-pressure pump

Feed and concentrate pressure, differential pressure across the membrane stage(s), low-flow alarm, and automatic alarm/shutdown at high permeate conductivity

OPERATIONAL RESILIENCE

Rated for continuous operation at the stated feed water quality without membrane scaling, provided antiscalant dosing and the specified CIP schedule are maintained

Dry-contact/signal interface for integration with an external clean-water buffer/accumulator tank, to enable hybrid blending with Na-cation softened water

Automatic safe shutdown on power loss; automatic membrane flush with permeate on restart (mains or generator power)

SUMMER PRESERVATION

Chemical membrane preservation agent(s) and a written protocol for a 5-6 month seasonal (summer) shutdown, to prevent bio-fouling and drying of the membrane elements

The protocol shall include at least one interim inspection during the shutdown period (with re-dosing/recirculation of the preservation solution if required by its condition and ambient temperature), rather than a single one-off lay-up only; bidder to state the proposed preservation product's validated hold time and the resulting inspection/re-dosing interval (typically every 3-6 months depending on temperature)

The preservation and recommissioning protocol (to be submitted with the offer) shall contain at least: (1) preparation of the unit before shutdown; (2) cleaning of the membranes; (3) selection and dosing of the preservative; (4) filling and circulation; (5) storage conditions; (6) required temperature limits; (7) interim inspection during the shutdown period; (8) criteria for re-dosing; (9) procedure for re-dosing or renewed circulation; (10) procedure for recommissioning and flushing; a one-off preservation without interim inspection is not sufficient

SCOPE OF SUPPLY (per unit)

Complete skid as specified above, factory tested

Training: online, minimum 1 full working day: operation, CIP washing procedure, seasonal membrane preservation/reactivation including interim inspection, calibration of pH and EC sensors, integration with the utility's existing water treatment scheme and control system, troubleshooting and safety; training materials and an attendance record to be provided

Operation & Maintenance manual and as-built documentation, in Ukrainian and/or English

Prices are stated as separate positions: equipment (1.1), online training (1.2) and consumables (1.3)

Consumables and spare parts for the first 2 years.

Completeness: the contractor is obliged to offer all components required for the complete, safe and ready-for-operation functioning of the unit within its limits of supply, even if these are not expressly named in individual items; external balance-of-plant components (in particular transfer pumps for the buffer/accumulator tank) and any treatment upstream of the unit's inlet (e.g. iron removal, softening) are not part of the supply

FACTORY ACCEPTANCE TEST

Each unit shall be tested at the factory before dispatch: pressure/leak test, functional test of the PLC, instruments, interlocks and dosing systems; a factory test report shall be supplied with each unit

The guaranteed values (permeate flow, salt rejection, operating pressure, specific energy consumption) shall be stated in the offer; their verification at site commissioning will be agreed in the next procurement round

WARRANTY

Min. 24 months on the equipment/skid (mechanical, electrical, PLC/instrumentation) from commissioning

Membrane element performance warranty per manufacturer's standard terms, applied against the feed water quality declared above

Warranty service (repair or replacement of defective parts) shall be provided by the supplier or its authorised service partner in Ukraine; the bidder shall name the partner (company, location) in the offer

INFORMATION TO BE PROVIDED WITH THE OFFER

Brand, manufacturer, model and type of the offered unit

Overall dimensions, weight and required installation footprint

Electrical connection data (voltage, installed power)

Make/model of the main components: cartridge housing, antiscalant and NaOH dosing pumps, high-pressure pump and VFD (rated power), membrane elements, pH/EC sensors, PLC/HMI

List of available signals and interfaces for SCADA integration

Number of packages/transport units, dimensions and gross weight per unit (for transport planning)

## 1.2. Training of utility staff (online) - RO unit 5 m3/h

TRAINING (per unit of position 1.1)

As specified under SCOPE OF SUPPLY - Training (position 1.1): minimum 1 full working day, online

Price per unit, stated separately from the equipment price

## 1.3. Consumables

Please specify what kind of consumables are required for the proper operation under Ukrainian circumstances. List them and add current prices for each item. The package must include a 2 year supply including 1.3.1 – 1.3.6.

It is expected to use the RO devices during heating season only (October – April), calculate with about 3.000 hours run time/a.

## 1.3.1 5-micron sediment pre-filter cartridges — 2-year operational supply (per installed 5 m³/h RO unit, Lot 1)

COMPATIBILITY

Replacement cartridges compatible with the pre-filtration stage of the RO unit specified under Lot 1 (5 m3/h); bidder to indicate compatible make/model in the technical offer

SPECIFICATION

Rating: 5 micron (nominal or absolute, to match the installed housing)

Material: polypropylene (PP), melt-blown or pleated, or equivalent, resistant to fouling by iron

Standard industrial length/diameter dimensions fitting a quick-release multi-cartridge housing

Individually packaged, boxed for storage; shelf-life min. 24 months from production date

QUANTITY BASIS ("set" = 2-year supply for 1 installed unit)

Bidder to state the assumed cartridge replacement frequency for the stated feed water quality (typical interval for high-iron Ukrainian DH raw water: every 2-6 weeks) and calculate the resulting total cartridge count in one 2-year "set", in the technical offer

## 1.3.2 Antiscalant dosing chemical — 2-year operational supply (per installed 5 m³/h RO unit, Lot 1)

COMPATIBILITY & PERFORMANCE

Liquid antiscalant/dispersant compatible with the polyamide TFC membranes specified under Lot 1

Effective for the stated design feed water: hardness up to 20 mg-eq/dm3, TDS up to 1,500 mg/dm3, iron up to 1.2 mg/dm3

Compatible with the digital diaphragm dosing pump specified under Lot 1

PACKAGING & DOCUMENTATION

Supplied in original manufacturer packaging (drums/canisters); shelf-life min. 24 months from production date

Safety Data Sheet (SDS) in English and/or Ukrainian to be provided

QUANTITY BASIS ("set" = 2-year supply for 1 installed unit)

Bidder to state the proposed dosing rate (ppm relative to feed flow) and calculate the resulting 2-year consumption volume (litres), for the design feed flow of the associated unit (5 m3/h permeate, Lot 1), in the technical offer

## 1.3.3. CIP cleaning chemicals — acid and alkaline agents, 2-year operational supply (per installed 5 m³/h RO unit, Lot 1)

SCOPE

Low-pH (acid) cleaning agent for removal of scale/iron fouling, compatible with the installed polyamide membranes specified under Lot 1

High-pH (alkaline) cleaning agent for removal of organic/biological fouling, compatible with the same membranes

PACKAGING & DOCUMENTATION

Original manufacturer packaging; shelf-life min. 24 months from production date

Safety Data Sheet (SDS) in English and/or Ukrainian to be provided for each chemical

QUANTITY BASIS ("set" = 2-year supply for 1 installed unit)

Bidder to state the proposed CIP cleaning frequency (e.g. once every 1-3 months, justified against the stated feed water quality) and the CIP tank volume of the offered unit, and calculate the resulting 2-year consumption (kg or L) of each chemical, in the technical offer

## 1.3.4. pH correction reagent (NaOH) — 2-year operational supply (per installed 5 m³/h RO unit, Lot 1)

SPECIFICATION

Sodium hydroxide (NaOH), technical/industrial grade suitable for water pH correction; liquid solution (e.g. 25-30%) or solid (pellets/flakes) form, as proposed by the bidder

Compatible with the pH-correction dosing pump specified under Lot 1

PACKAGING & DOCUMENTATION

Appropriate secondary containment/packaging for a caustic chemical; shelf-life min. 24 months from production date

Safety Data Sheet (SDS) in English and/or Ukrainian to be provided

QUANTITY BASIS ("set" = 2-year supply for 1 installed unit)

Bidder to state the proposed dosing rate required to raise permeate pH from approx. 5.0-5.3 to 8.5-9.5, at the design permeate flow of the associated unit (5 m3/h, Lot 1), and calculate the resulting 2-year consumption, in the technical offer

## 1.3.5. Membrane preservation/conservation chemical kit — seasonal, 2-year operational supply (per installed 5 m³/h RO unit, Lot 1)

SCOPE

Chemical preservation/conservation agent for the seasonal (5-6 month, summer) shutdown of the RO unit specified under Lot 1, to prevent biological fouling and drying of the membrane elements

Written preservation and reactivation protocol specific to the membrane elements installed, to be provided with the first delivery

QUANTITY BASIS ("set" = 2-year supply, i.e. 2 seasonal preservation cycles, for 1 installed unit)

Bidder to state the assumed membrane pressure vessel volume and the resulting preservation chemical volume required per cycle, in the technical offer

PACKAGING & DOCUMENTATION

Original manufacturer packaging; shelf-life min. 24 months from production date

Safety Data Sheet (SDS) in English and/or Ukrainian to be provided

## 1.3.6. Critical mechanical/instrumentation spare parts kit — 2-year operational supply (per installed 5 m³/h RO unit, Lot 1)

SCOPE

Shaft seals / mechanical seals for the high-pressure pump (quantity for the number of scheduled seal changes over 2 years, per manufacturer's maintenance schedule)

Diaphragms/membranes (wearing parts) for the antiscalant and pH-correction dosing pumps - 1 full replacement set per pump

Spare pH sensor and spare electrical conductivity (EC) sensor, compatible with the PLC/instrumentation specified under Lot 1 - 1 of each

Gasket/O-ring set for the cartridge filter housing - sufficient for all scheduled cartridge changes over 2 years

PACKAGING & DOCUMENTATION

Original manufacturer packaging, individually labelled per part; shelf-life min. 24 months from production date

Parts list cross-referenced to the equipment supplied under Lot 1 (position/drawing reference)

QUANTITY BASIS ("set" = 2-year supply for 1 installed unit)

Bidder to state, for each part, the assumed replacement interval / expected service life under the stated feed water and operating conditions, and the resulting quantity included in one 2-year "set", in the technical offer

## 2.1. Lot 2: Reverse Osmosis (RO) Water Treatment Unit, 10 m3/h permeate capacity (skid-mounted, complete system) - equipment

GENERAL

Skid-mounted, fully automated, factory pre-assembled and pre-tested reverse osmosis (RO) water treatment unit for district heating (DH) make-up water treatment

Suitable for indoor installation and continuous operation at DH utility sites in Ukraine

Nominal permeate capacity: 10 m3/h at the reference feed water quality stated below

Recovery rate: minimum 75% (an outcome of the bidder's project-specific design calculation for the stated feed water quality; see MEMBRANE BLOCK and HIGH-PRESSURE PUMP below - not a fixed band)

Bidder shall submit a project-specific membrane design/projection report (e.g. ROSA, IMSDesign or equivalent) confirming the offered configuration meets this capacity at the stated feed water quality

The report shall contain at least: raw water quality and design temperature; membrane type and manufacturer; number of pressure vessels and membrane elements; membrane area and array; design flux; permeate and concentrate flow; recovery; operating pressure; permeate quality and salt rejection; expected ion concentrations and saturation indices in the concentrate (CaCO3, CaSO4, BaSO4, SrSO4, SiO2); required antiscalant dosing; specific energy consumption and its basis of calculation. It shall be based on the worst-case raw water quality stated above; the bidder shall name any further water analyses required for the final membrane design

FEED WATER DESIGN BASIS (worst-case Ukrainian DH raw water)

Total hardness: up to 20 mg-eq/dm3

Total dissolved solids (TDS): up to 1,500 mg/dm3

Iron content: up to 1.2 mg/dm3

The bidder shall state the further feed water parameters assumed in the design (temperature range, pH, alkalinity, calcium, magnesium, sulphate, silica, chloride, sodium, manganese, turbidity, SDI); site-specific raw water analyses shall be checked before commissioning

The bidder shall state the maximum allowable RO-inlet values required by the membrane manufacturer (total and dissolved iron, manganese, SDI, turbidity, residual oxidants); meeting these values by upstream treatment (e.g. iron removal) is the responsibility of the DH utility

PRE-FILTRATION

5-micron sediment cartridge filters, heavy-duty, quick-replace multi-cartridge housing, sized for full design flow

ANTISCALANT DOSING

Digital diaphragm metering pump with proportional (flow-paced) dosing control

Dedicated chemical day-tank with low-level alarm

Antiscalant formulation compatible with the stated hardness/iron/TDS

HIGH-PRESSURE PUMP

Multistage pump, stainless steel wetted parts (min. AISI 316), with Variable Frequency Drive (VFD)

Operating pressure is an outcome of the bidder's project-specific membrane design calculation for the stated feed water quality, the specified flux limit and the selected recovery (indicative reference range for this water quality: 14-18 bar; not a fixed requirement)

Specific energy consumption: to be calculated by the bidder and stated as a guaranteed value (kWh/m3 of permeate) at clean membranes and design temperature, measured at the skid boundary (high-pressure pump plus all auxiliary/dosing drives mounted on the skid; excludes external balance-of-plant equipment such as buffer-tank transfer pumps); to be provided together with the supporting pump curve and system energy balance specific to the offered 10 m3/h capacity, and documented in the factory test report (see FACTORY ACCEPTANCE TEST below)

MEMBRANE BLOCK

High-rejection, fouling-resistant polyamide thin-film composite (TFC) spiral-wound elements; commercially available and replaceable from more than one manufacturer (no proprietary/non-standard format); element diameter (4-inch or 8-inch) to be selected by the bidder as appropriate for the offered capacity and array design, and justified in the design calculation

Minimum nominal salt (NaCl) rejection per element: 99.5%, per manufacturer's standard test conditions

Maximum average design permeate flux: 18 L/(m2*h), appropriate for iron-bearing feed water; bidder to state the number of elements/pressure vessels and the resulting design flux in the technical offer

Recovery: minimum 75% (bidder may propose a higher design recovery where justified by the feed water quality, flux limit and element selection)

Bidder to state expected element life under the stated feed water (indicative range: 2-3 years, versus a 5-6 year nominal design life, due to the aggressive raw water)

pH CORRECTION (CO2 NEUTRALIZATION)

Dedicated NaOH dosing pump and day-tank on the permeate line

Function: neutralize free CO2 and raise permeate pH from approx. 5.0-5.3 to 8.5-9.5

Automatic, pH-controlled proportional dosing, interlocked with an online permeate pH sensor

Residual free CO2 is removed in the utility's existing thermal deaeration (not part of the supply); the bidder shall state the expected free CO2 concentration in the permeate and the resulting NaOH consumption

CLEAN-IN-PLACE (CIP) SYSTEM

Fully integrated CIP station: cleaning tank, circulation pump, cartridge pre-filter, valves and piping for both low-pH (acid) and high-pH (alkaline) cleaning cycles

Cleaning cycle sequencing via the PLC (automatic or semi-automatic)

INSTRUMENTATION & CONTROL (PLC)

PLC controller with colour touchscreen HMI

Continuous online monitoring and PLC logging of: electrical conductivity (EC) of raw water and permeate; temperature; pH of raw water and permeate; permeate and concentrate flow rates

4-20 mA and/or dry-contact outputs for remote monitoring/SCADA integration

Automatic low-pressure, high-pressure and dry-run protection interlocks on the high-pressure pump

Feed and concentrate pressure, differential pressure across the membrane stage(s), low-flow alarm, and automatic alarm/shutdown at high permeate conductivity

OPERATIONAL RESILIENCE

Rated for continuous operation at the stated feed water quality without membrane scaling, provided antiscalant dosing and the specified CIP schedule are maintained

Dry-contact/signal interface for integration with an external clean-water buffer/accumulator tank, to enable hybrid blending with Na-cation softened water

Automatic safe shutdown on power loss; automatic membrane flush with permeate on restart (mains or generator power)

SUMMER PRESERVATION

Chemical membrane preservation agent(s) and a written protocol for a 5-6 month seasonal (summer) shutdown, to prevent bio-fouling and drying of the membrane elements

The protocol shall include at least one interim inspection during the shutdown period (with re-dosing/recirculation of the preservation solution if required by its condition and ambient temperature), rather than a single one-off lay-up only; bidder to state the proposed preservation product's validated hold time and the resulting inspection/re-dosing interval (typically every 3-6 months depending on temperature)

The preservation and recommissioning protocol (to be submitted with the offer) shall contain at least: (1) preparation of the unit before shutdown; (2) cleaning of the membranes; (3) selection and dosing of the preservative; (4) filling and circulation; (5) storage conditions; (6) required temperature limits; (7) interim inspection during the shutdown period; (8) criteria for re-dosing; (9) procedure for re-dosing or renewed circulation; (10) procedure for recommissioning and flushing; a one-off preservation without interim inspection is not sufficient

SCOPE OF SUPPLY (per unit)

Complete skid as specified above, factory tested

Training: online, minimum 1 full working day: operation, CIP washing procedure, seasonal membrane preservation/reactivation including interim inspection, calibration of pH and EC sensors, integration with the utility's existing water treatment scheme and control system, troubleshooting and safety; training materials and an attendance record to be provided

Operation & Maintenance manual and as-built documentation, in Ukrainian and/or English

Prices are stated as separate positions: equipment (2.1), online training (2.2) and consumables (2.3)

Consumables and spare parts for the first 2 years

Completeness: the contractor is obliged to offer all components required for the complete, safe and ready-for-operation functioning of the unit within its limits of supply, even if these are not expressly named in individual items; external balance-of-plant components (in particular transfer pumps for the buffer/accumulator tank) and any treatment upstream of the unit's inlet (e.g. iron removal, softening) are not part of the supply

FACTORY ACCEPTANCE TEST

Each unit shall be tested at the factory before dispatch: pressure/leak test, functional test of the PLC, instruments, interlocks and dosing systems; a factory test report shall be supplied with each unit

The guaranteed values (permeate flow, salt rejection, operating pressure, specific energy consumption) shall be stated in the offer; their verification at site commissioning will be agreed in the next procurement round

WARRANTY

Min. 24 months on the equipment/skid (mechanical, electrical, PLC/instrumentation) from commissioning

Membrane element performance warranty per manufacturer's standard terms, applied against the feed water quality declared above

Warranty service (repair or replacement of defective parts) shall be provided by the supplier or its authorised service partner in Ukraine; the bidder shall name the partner (company, location) in the offer

INFORMATION TO BE PROVIDED WITH THE OFFER

Brand, manufacturer, model and type of the offered unit

Overall dimensions, weight and required installation footprint

Electrical connection data (voltage, installed power)

Make/model of the main components: cartridge housing, antiscalant and NaOH dosing pumps, high-pressure pump and VFD (rated power), membrane elements, pH/EC sensors, PLC/HMI

List of available signals and interfaces for SCADA integration

Number of packages/transport units, dimensions and gross weight per unit (for transport planning)

## 2.2. Training of utility staff (online) - RO unit 10 m3/h

TRAINING (per unit of position 2.1)

As specified under SCOPE OF SUPPLY - Training (position 2.1): minimum 1 full working day, online

Price per unit, stated separately from the equipment price

## 2.3. Consumables

Please specify what kind of consumables are required for the proper operation under Ukrainian circumstances. List them and add current prices for each item. The package must include a 2 year supply including 2.3.1 – 2.3.5

It is expected to use the RO devices during heating season only (October – April), calculate with about 3.000 hours run time/a.

## 2.3.1 5-micron sediment pre-filter cartridges — 2-year operational supply (per installed 10 m³/h RO unit, Lot 2)

COMPATIBILITY

Replacement cartridges compatible with the pre-filtration stage of the RO unit specified under Lot 2 (10 m3/h); bidder to indicate compatible make/model in the technical offer

SPECIFICATION

Rating: 5 micron (nominal or absolute, to match the installed housing)

Material: polypropylene (PP), melt-blown or pleated, or equivalent, resistant to fouling by iron

Standard industrial length/diameter dimensions fitting a quick-release multi-cartridge housing

Individually packaged, boxed for storage; shelf-life min. 24 months from production date

QUANTITY BASIS ("set" = 2-year supply for 1 installed unit)

Bidder to state the assumed cartridge replacement frequency for the stated feed water quality (typical interval for high-iron Ukrainian DH raw water: every 2-6 weeks) and calculate the resulting total cartridge count in one 2-year "set", in the technical offer

## 2.3.2. Antiscalant dosing chemical — 2-year operational supply (per installed 10 m³/h RO unit, Lot 2)

COMPATIBILITY & PERFORMANCE

Liquid antiscalant/dispersant compatible with the polyamide TFC membranes specified under Lot 2

Effective for the stated design feed water: hardness up to 20 mg-eq/dm3, TDS up to 1,500 mg/dm3, iron up to 1.2 mg/dm3

Compatible with the digital diaphragm dosing pump specified under Lot 2

PACKAGING & DOCUMENTATION

Supplied in original manufacturer packaging (drums/canisters); shelf-life min. 24 months from production date

Safety Data Sheet (SDS) in English and/or Ukrainian to be provided

QUANTITY BASIS ("set" = 2-year supply for 1 installed unit)

Bidder to state the proposed dosing rate (ppm relative to feed flow) and calculate the resulting 2-year consumption volume (litres), for the design feed flow of the associated unit (10 m3/h permeate, Lot 2), in the technical offer

## 2.3.3. CIP cleaning chemicals — acid and alkaline agents, 2-year operational supply (per installed 10 m³/h RO unit, Lot 2)

SCOPE

Low-pH (acid) cleaning agent for removal of scale/iron fouling, compatible with the installed polyamide membranes specified under Lot 2

High-pH (alkaline) cleaning agent for removal of organic/biological fouling, compatible with the same membranes

PACKAGING & DOCUMENTATION

Original manufacturer packaging; shelf-life min. 24 months from production date

Safety Data Sheet (SDS) in English and/or Ukrainian to be provided for each chemical

QUANTITY BASIS ("set" = 2-year supply for 1 installed unit)

Bidder to state the proposed CIP cleaning frequency (e.g. once every 1-3 months, justified against the stated feed water quality) and the CIP tank volume of the offered unit, and calculate the resulting 2-year consumption (kg or L) of each chemical, in the technical offer

## 2.3.4. pH correction reagent (NaOH) — 2-year operational supply (per installed 10 m³/h RO unit, Lot 2)

SPECIFICATION

Sodium hydroxide (NaOH), technical/industrial grade suitable for water pH correction; liquid solution (e.g. 25-30%) or solid (pellets/flakes) form, as proposed by the bidder

Compatible with the pH-correction dosing pump specified under Lot 2

PACKAGING & DOCUMENTATION

Appropriate secondary containment/packaging for a caustic chemical; shelf-life min. 24 months from production date

Safety Data Sheet (SDS) in English and/or Ukrainian to be provided

QUANTITY BASIS ("set" = 2-year supply for 1 installed unit)

Bidder to state the proposed dosing rate required to raise permeate pH from approx. 5.0-5.3 to 8.5-9.5, at the design permeate flow of the associated unit (10 m3/h, Lot 2), and calculate the resulting 2-year consumption, in the technical offer

## 2.3.5. Membrane preservation/conservation chemical kit — seasonal, 2-year operational supply (per installed 10 m³/h RO unit, Lot 2)

SCOPE

Chemical preservation/conservation agent for the seasonal (5-6 month, summer) shutdown of the RO unit specified under Lot 2, to prevent biological fouling and drying of the membrane elements

Written preservation and reactivation protocol specific to the membrane elements installed, to be provided with the first delivery

QUANTITY BASIS ("set" = 2-year supply, i.e. 2 seasonal preservation cycles, for 1 installed unit)

Bidder to state the assumed membrane pressure vessel volume and the resulting preservation chemical volume required per cycle, in the technical offer

PACKAGING & DOCUMENTATION

Original manufacturer packaging; shelf-life min. 24 months from production date

Safety Data Sheet (SDS) in English and/or Ukrainian to be provided

## 2.3.6. Critical mechanical/instrumentation spare parts kit — 2-year operational supply (per installed 10 m³/h RO unit, Lot 2)

SCOPE

Shaft seals / mechanical seals for the high-pressure pump (quantity for the number of scheduled seal changes over 2 years, per manufacturer's maintenance schedule)

Diaphragms/membranes (wearing parts) for the antiscalant and pH-correction dosing pumps - 1 full replacement set per pump

Spare pH sensor and spare electrical conductivity (EC) sensor, compatible with the PLC/instrumentation specified under Lot 2 - 1 of each

Gasket/O-ring set for the cartridge filter housing - sufficient for all scheduled cartridge changes over 2 years

PACKAGING & DOCUMENTATION

Original manufacturer packaging, individually labelled per part; shelf-life min. 24 months from production date

Parts list cross-referenced to the equipment supplied under Lot 2 (position/drawing reference)

QUANTITY BASIS ("set" = 2-year supply for 1 installed unit)

Bidder to state, for each part, the assumed replacement interval / expected service life under the stated feed water and operating conditions, and the resulting quantity included in one 2-year "set", in the technical offer