## Specification Lots 1,2,3
Lot | Position | Item description |  | Quantity [pcs.] | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns B-E, please indicate "Yes". Otherwise, describe your special features in this column. | Unit cost, EUR |  | Control Panel Unit cost, EUR
all lots |  | General requirement | Availability of an authorized service center in Ukraine. In the event of a warranty case, the center must resolve the issue within 60 days from the date of application.
1 | 1.1 | Flanged gate valve, DN400 | FLANGED RESILIENT-SEATED WEDGE GATE VALVE – PN10 For potable water, raw water and treated wastewater Application:Potable water, raw water and treated wastewater/effluent with low content of suspended solids and fibrous impurities. Pressure rating:PN10. Valve type:Flanged resilient-seated wedge gate valve for isolation service. Body and bonnet:Ductile iron or equivalent material suitable for PN10 service conditions. Wedge:Ductile iron wedge, fully encapsulated/vulcanized with EPDM or equivalent elastomer suitable for the specified operating medium. Elastomer shall be suitable for potable-water applications where applicable. Stem:Non-rising stem made of stainless steel or equivalent corrosion-resistant material. Stem sealing:Reliable sealing system suitable for the specified pressure, temperature and operating medium. Bolting:Corrosion-resistant material suitable for the service conditions. Corrosion protection:Factory-applied fusion-bonded epoxy or equivalent heavy-duty corrosion-protection system suitable for buried and/or external installation. Coating shall comply with EN 14901-1 or an equivalent recognized standard. Flanged connection:Flanged ends according to EN 1092-2, PN10. Face-to-face dimensions:According to EN 558, Series 14 (F4). Design and performance:EN 1074-1 and EN 1074-2; EN 1171 where applicable. Seat tightness:The closed valve shall provide tight shut-off in accordance with the applicable requirements of EN 12266-1, with no visible leakage under the specified test conditions. Operating temperature:Suitable for the specified water/wastewater service, approximately 0 °C to +70 °C. Operating conditions:The valve shall be capable of safe opening and closing at the specified operating pressure and the maximum differential pressure declared by the manufacturer. Operating torque:The manufacturer shall declare the maximum operating torque and, where applicable, the torque required for gearbox or actuator selection. Actuation:Handwheel for manual operation as standard. The valve shall be suitable for installation of a gearbox or electric actuator where required. Installation:The valve shall be supplied complete and suitable for installation in accordance with the manufacturer's standard installation requirements. Potable-water compliance:Where used in potable-water systems, all materials, elastomers and coatings in contact with drinking water shall comply with applicable national/EU requirements. Recognized drinking-water approval or equivalent conformity may be provided. | 70 |  | 2800
| 1.2 | Flanged gate valve, DN500 | FLANGED RESILIENT-SEATED WEDGE GATE VALVE – PN10 For potable water, raw water and treated wastewater Application:Potable water, raw water and treated wastewater/effluent with low content of suspended solids and fibrous impurities. Pressure rating:PN10. Valve type:Flanged resilient-seated wedge gate valve for isolation service. Body and bonnet:Ductile iron or equivalent material suitable for PN10 service conditions. Wedge:Ductile iron wedge, fully encapsulated/vulcanized with EPDM or equivalent elastomer suitable for the specified operating medium. Elastomer shall be suitable for potable-water applications where applicable. Stem:Non-rising stem made of stainless steel or equivalent corrosion-resistant material. Stem sealing:Reliable sealing system suitable for the specified pressure, temperature and operating medium. Bolting:Corrosion-resistant material suitable for the service conditions. Corrosion protection:Factory-applied fusion-bonded epoxy or equivalent heavy-duty corrosion-protection system suitable for buried and/or external installation. Coating shall comply with EN 14901-1 or an equivalent recognized standard. Flanged connection:Flanged ends according to EN 1092-2, PN10. Face-to-face dimensions:According to EN 558, Series 14 (F4). Design and performance:EN 1074-1 and EN 1074-2; EN 1171 where applicable. Seat tightness:The closed valve shall provide tight shut-off in accordance with the applicable requirements of EN 12266-1, with no visible leakage under the specified test conditions. Operating temperature:Suitable for the specified water/wastewater service, approximately 0 °C to +70 °C. Operating conditions:The valve shall be capable of safe opening and closing at the specified operating pressure and the maximum differential pressure declared by the manufacturer. Operating torque:The manufacturer shall declare the maximum operating torque and, where applicable, the torque required for gearbox or actuator selection. Actuation:Handwheel for manual operation as standard. The valve shall be suitable for installation of a gearbox or electric actuator where required. Installation:The valve shall be supplied complete and suitable for installation in accordance with the manufacturer's standard installation requirements. Potable-water compliance:Where used in potable-water systems, all materials, elastomers and coatings in contact with drinking water shall comply with applicable national/EU requirements. Recognized drinking-water approval or equivalent conformity may be provided. | 16 |  | 4300
| 1.3 | Flanged gate valve, DN600 | FLANGED RESILIENT-SEATED WEDGE GATE VALVE – PN10 For potable water, raw water and treated wastewater Application:Potable water, raw water and treated wastewater/effluent with low content of suspended solids and fibrous impurities. Pressure rating:PN10. Valve type:Flanged resilient-seated wedge gate valve for isolation service. Body and bonnet:Ductile iron or equivalent material suitable for PN10 service conditions. Wedge:Ductile iron wedge, fully encapsulated/vulcanized with EPDM or equivalent elastomer suitable for the specified operating medium. Elastomer shall be suitable for potable-water applications where applicable. Stem:Non-rising stem made of stainless steel or equivalent corrosion-resistant material. Stem sealing:Reliable sealing system suitable for the specified pressure, temperature and operating medium. Bolting:Corrosion-resistant material suitable for the service conditions. Corrosion protection:Factory-applied fusion-bonded epoxy or equivalent heavy-duty corrosion-protection system suitable for buried and/or external installation. Coating shall comply with EN 14901-1 or an equivalent recognized standard. Flanged connection:Flanged ends according to EN 1092-2, PN10. Face-to-face dimensions:According to EN 558, Series 14 (F4). Design and performance:EN 1074-1 and EN 1074-2; EN 1171 where applicable. Seat tightness:The closed valve shall provide tight shut-off in accordance with the applicable requirements of EN 12266-1, with no visible leakage under the specified test conditions. Operating temperature:Suitable for the specified water/wastewater service, approximately 0 °C to +70 °C. Operating conditions:The valve shall be capable of safe opening and closing at the specified operating pressure and the maximum differential pressure declared by the manufacturer. Operating torque:The manufacturer shall declare the maximum operating torque and, where applicable, the torque required for gearbox or actuator selection. Actuation:Handwheel for manual operation as standard. The valve shall be suitable for installation of a gearbox or electric actuator where required. Installation:The valve shall be supplied complete and suitable for installation in accordance with the manufacturer's standard installation requirements. Potable-water compliance:Where used in potable-water systems, all materials, elastomers and coatings in contact with drinking water shall comply with applicable national/EU requirements. Recognized drinking-water approval or equivalent conformity may be provided. | 90 |  | 6500 |  |  | #REF!
| 1.4 | Flanged gate valve, DN400 | FLANGED RESILIENT-SEATED WEDGE GATE VALVE – PN16 For potable water supply systems Application:Potable water supply and distribution systems. Pressure rating:PN16. Valve type:Flanged resilient-seated wedge gate valve for isolation service. Body and bonnet:Ductile iron or equivalent material suitable for PN16 potable-water service conditions. Wedge:Ductile iron wedge, fully encapsulated/vulcanized with EPDM or equivalent elastomer suitable for potable water. Stem:Non-rising stem made of stainless steel or equivalent corrosion-resistant material. Stem sealing:Reliable sealing system suitable for PN16 potable-water service. Bolting:Corrosion-resistant material suitable for the service conditions. Corrosion protection:Factory-applied fusion-bonded epoxy or equivalent heavy-duty corrosion-protection system suitable for buried and/or external installation. Coating shall comply with EN 14901-1 or an equivalent recognized standard. Flanged connection:Flanged ends according to EN 1092-2, PN16. Face-to-face dimensions:According to EN 558, Series 14 (F4). Design and performance:EN 1074-1 and EN 1074-2; EN 1171 where applicable. Testing:Production testing according to EN 12266-1 or equivalent recognized standard. The closed valve shall provide tight shut-off in accordance with the applicable requirements of EN 12266-1, with no visible leakage under the specified test conditions. Operating temperature:Suitable for potable-water service, approximately 0 °C to +70 °C. Operating conditions:The valve shall be capable of safe opening and closing at PN16 and at the maximum differential pressure declared by the manufacturer. Operating torque:The manufacturer shall declare the maximum operating torque and, where applicable, the torque required for gearbox or actuator selection. Actuation:Handwheel for manual operation as standard. The valve shall be suitable for installation of a gearbox or electric actuator where required. Installation:Suitable for installation in valve chambers Potable-water compliance:All wetted materials, elastomers and coatings shall comply with applicable requirements for potable-water contact. Recognized drinking-water approval/certification such as WRAS, ACS, DVGW, KIWA, SVGW, Belgaqua or equivalent nationally/internationally recognized conformity shall be accepted. | 8 |  | 2700
| 1.5 | Flanged gate valve, DN500 | FLANGED RESILIENT-SEATED WEDGE GATE VALVE – PN16 For potable water supply systems Application:Potable water supply and distribution systems. Pressure rating:PN16. Valve type:Flanged resilient-seated wedge gate valve for isolation service. Body and bonnet:Ductile iron or equivalent material suitable for PN16 potable-water service conditions. Wedge:Ductile iron wedge, fully encapsulated/vulcanized with EPDM or equivalent elastomer suitable for potable water. Stem:Non-rising stem made of stainless steel or equivalent corrosion-resistant material. Stem sealing:Reliable sealing system suitable for PN16 potable-water service. Bolting:Corrosion-resistant material suitable for the service conditions. Corrosion protection:Factory-applied fusion-bonded epoxy or equivalent heavy-duty corrosion-protection system suitable for buried and/or external installation. Coating shall comply with EN 14901-1 or an equivalent recognized standard. Flanged connection:Flanged ends according to EN 1092-2, PN16. Face-to-face dimensions:According to EN 558, Series 14 (F4). Design and performance:EN 1074-1 and EN 1074-2; EN 1171 where applicable. Testing:Production testing according to EN 12266-1 or equivalent recognized standard. The closed valve shall provide tight shut-off in accordance with the applicable requirements of EN 12266-1, with no visible leakage under the specified test conditions. Operating temperature:Suitable for potable-water service, approximately 0 °C to +70 °C. Operating conditions:The valve shall be capable of safe opening and closing at PN16 and at the maximum differential pressure declared by the manufacturer. Operating torque:The manufacturer shall declare the maximum operating torque and, where applicable, the torque required for gearbox or actuator selection. Actuation:Handwheel for manual operation as standard. The valve shall be suitable for installation of a gearbox or electric actuator where required. Installation:Suitable for installation in valve chambers Potable-water compliance:All wetted materials, elastomers and coatings shall comply with applicable requirements for potable-water contact. Recognized drinking-water approval/certification such as WRAS, ACS, DVGW, KIWA, SVGW, Belgaqua or equivalent nationally/internationally recognized conformity shall be accepted. | 6 |  | 4300
| 1.6 | Flanged gate valve, DN600 | FLANGED RESILIENT-SEATED WEDGE GATE VALVE – PN16 For potable water supply systems Application:Potable water supply and distribution systems. Pressure rating:PN16. Valve type:Flanged resilient-seated wedge gate valve for isolation service. Body and bonnet:Ductile iron or equivalent material suitable for PN16 potable-water service conditions. Wedge:Ductile iron wedge, fully encapsulated/vulcanized with EPDM or equivalent elastomer suitable for potable water. Stem:Non-rising stem made of stainless steel or equivalent corrosion-resistant material. Stem sealing:Reliable sealing system suitable for PN16 potable-water service. Bolting:Corrosion-resistant material suitable for the service conditions. Corrosion protection:Factory-applied fusion-bonded epoxy or equivalent heavy-duty corrosion-protection system suitable for buried and/or external installation. Coating shall comply with EN 14901-1 or an equivalent recognized standard. Flanged connection:Flanged ends according to EN 1092-2, PN16. Face-to-face dimensions:According to EN 558, Series 14 (F4). Design and performance:EN 1074-1 and EN 1074-2; EN 1171 where applicable. Testing:Production testing according to EN 12266-1 or equivalent recognized standard. The closed valve shall provide tight shut-off in accordance with the applicable requirements of EN 12266-1, with no visible leakage under the specified test conditions. Operating temperature:Suitable for potable-water service, approximately 0 °C to +70 °C. Operating conditions:The valve shall be capable of safe opening and closing at PN16 and at the maximum differential pressure declared by the manufacturer. Operating torque:The manufacturer shall declare the maximum operating torque and, where applicable, the torque required for gearbox or actuator selection. Actuation:Handwheel for manual operation as standard. The valve shall be suitable for installation of a gearbox or electric actuator where required. Installation:Suitable for installation in valve chambers Potable-water compliance:All wetted materials, elastomers and coatings shall comply with applicable requirements for potable-water contact. Recognized drinking-water approval/certification such as WRAS, ACS, DVGW, KIWA, SVGW, Belgaqua or equivalent nationally/internationally recognized conformity shall be accepted. | 17 |  | 6600 |  |  | #REF! | #REF!
2 | 2.1 | Sewage pump Q= 250 m³/h, H=30-40m | Application: Municipal sewage pumping stations (KNS) for untreated or partially screened wastewater containing faecal matter, suspended, fibrous solids, and abrasive sand/grit.2 Pump type: Horizontal centrifugal sewage pump for dry-pit/dry-well installation, mounted on a common steel or cast iron baseframe. Installation: Dry installation outside the pumped liquid. Back Pull-Out design or equivalent allowing rotating element maintenance without disconnecting the casing from pipework. Operating point: As specified in the Schedule of Requirements Pump design: Non-clog sewage pump suitable for reliable operation with municipal wastewater Impeller: Single-channel, multi-channel, or equivalent non-clog design with hydraulic efficiency minimum 78-80% at BEP. Dynamically balanced. Free passage: Minimum 80 mm (or minimum 100 mm for capacities up to 500 m³/h). Liquid temperature: Maximum liquid temperature: minimum +40 °C. Pump materials: Wear-resistant cast iron (minimum EN-GJS-400 or equivalent wear-resistant alloy). Grey cast iron configurations must include replaceable wear components. Wear Protection: Replaceable wear rings or wear plates on the casing and/or impeller side. Shaft: Stainless steel (minimum AISI 431 or manufacturer's equivalent grade protected by a shaft sleeve). Mechanical seal:Double mechanical shaft seal operating in an oil chamber. Seal face materials on the liquid side shall be Silicon Carbide (SiC/SiC) or Tungsten Carbide. Oil chamber equipped with a leakage sensor. Bearings: Heavy-duty grease or oil-lubricated bearings with minimum L10 bearing life of 50,000 hours. Motor type: Three-phase squirrel-cage induction motor. Electrical data: Rated voltage: 400 V ±10 %. Rated frequency: 50 Hz. Motor efficiency: IE3 minimum according to IEC 60034-30-1. Insulation class: Class F minimum. Degree of protection: IP55-IP57 according to IEC 60034-5. If an IP68 motor is offered, it must include an integrated cooling jacket for continuous dry-run operation. Duty:Continuous duty, S1. Pump efficiency: Supplier shall declare hydraulic efficiency at the duty point. The duty point shall lie within the manufacturer's preferred operating range (close to BEP). Performance curve: Manufacturer's official Q-H, power consumption, and efficiency curves shall be submitted. Standards: EN 809 or equivalent for pump safety; IEC 60034 series or equivalent for the motor. Hydraulic testing and tolerances according to ISO 9906 (Class 2B or Class 1B). Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [45-50] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip). | 20 |  | 15000 | Frequency converter 45 - 50 kW | 3900
| 2.2 | Sewage pump Q= 250 m³/h, H=50-60m | Application: Municipal sewage pumping stations (KNS) for untreated or partially screened wastewater containing faecal matter, suspended, fibrous solids, and abrasive sand/grit.2 Pump type: Horizontal centrifugal sewage pump for dry-pit/dry-well installation, mounted on a common steel or cast iron baseframe. Installation: Dry installation outside the pumped liquid. Back Pull-Out design or equivalent allowing rotating element maintenance without disconnecting the casing from pipework. Operating point: As specified in the Schedule of Requirements Pump design: Non-clog sewage pump suitable for reliable operation with municipal wastewater Impeller: Single-channel, multi-channel, or equivalent non-clog design with hydraulic efficiency minimum 78-80% at BEP. Dynamically balanced. Free passage: Minimum 80 mm (or minimum 100 mm for capacities up to 500 m³/h). Liquid temperature: Maximum liquid temperature: minimum +40 °C. Pump materials: Wear-resistant cast iron (minimum EN-GJS-400 or equivalent wear-resistant alloy). Grey cast iron configurations must include replaceable wear components. Wear Protection: Replaceable wear rings or wear plates on the casing and/or impeller side. Shaft: Stainless steel (minimum AISI 431 or manufacturer's equivalent grade protected by a shaft sleeve). Mechanical seal:Double mechanical shaft seal operating in an oil chamber. Seal face materials on the liquid side shall be Silicon Carbide (SiC/SiC) or Tungsten Carbide. Oil chamber equipped with a leakage sensor. Bearings: Heavy-duty grease or oil-lubricated bearings with minimum L10 bearing life of 50,000 hours. Motor type: Three-phase squirrel-cage induction motor. Electrical data: Rated voltage: 400 V ±10 %. Rated frequency: 50 Hz. Motor efficiency: IE3 minimum according to IEC 60034-30-1. Insulation class: Class F minimum. Degree of protection: IP55-IP57 according to IEC 60034-5. If an IP68 motor is offered, it must include an integrated cooling jacket for continuous dry-run operation. Duty:Continuous duty, S1. Pump efficiency: Supplier shall declare hydraulic efficiency at the duty point. The duty point shall lie within the manufacturer's preferred operating range (close to BEP). Performance curve: Manufacturer's official Q-H, power consumption, and efficiency curves shall be submitted. Standards: EN 809 or equivalent for pump safety; IEC 60034 series or equivalent for the motor. Hydraulic testing and tolerances according to ISO 9906 (Class 2B or Class 1B). Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [75-80] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 14 |  | 22000 | Frequency converter 75 - 80 kW | 5800
| 2.3 | Sewage pump Q= 250 m³/h, H=90-100m | Application: Municipal sewage pumping stations (KNS) for untreated or partially screened wastewater containing faecal matter, suspended, fibrous solids, and abrasive sand/grit.2 Pump type: Horizontal centrifugal sewage pump for dry-pit/dry-well installation, mounted on a common steel or cast iron baseframe. Installation: Dry installation outside the pumped liquid. Back Pull-Out design or equivalent allowing rotating element maintenance without disconnecting the casing from pipework. Operating point: As specified in the Schedule of Requirements Pump design: Non-clog sewage pump suitable for reliable operation with municipal wastewater Impeller: Single-channel, multi-channel, or equivalent non-clog design with hydraulic efficiency minimum 78-80% at BEP. Dynamically balanced. Free passage: Minimum 80 mm (or minimum 100 mm for capacities up to 500 m³/h). Liquid temperature: Maximum liquid temperature: minimum +40 °C. Pump materials: Wear-resistant cast iron (minimum EN-GJS-400 or equivalent wear-resistant alloy). Grey cast iron configurations must include replaceable wear components. Wear Protection: Replaceable wear rings or wear plates on the casing and/or impeller side. Shaft: Stainless steel (minimum AISI 431 or manufacturer's equivalent grade protected by a shaft sleeve). Mechanical seal:Double mechanical shaft seal operating in an oil chamber. Seal face materials on the liquid side shall be Silicon Carbide (SiC/SiC) or Tungsten Carbide. Oil chamber equipped with a leakage sensor. Bearings: Heavy-duty grease or oil-lubricated bearings with minimum L10 bearing life of 50,000 hours. Motor type: Three-phase squirrel-cage induction motor. Electrical data: Rated voltage: 400 V ±10 %. Rated frequency: 50 Hz. Motor efficiency: IE3 minimum according to IEC 60034-30-1. Insulation class: Class F minimum. Degree of protection: IP55-IP57 according to IEC 60034-5. If an IP68 motor is offered, it must include an integrated cooling jacket for continuous dry-run operation. Duty:Continuous duty, S1. Pump efficiency: Supplier shall declare hydraulic efficiency at the duty point. The duty point shall lie within the manufacturer's preferred operating range (close to BEP). Performance curve: Manufacturer's official Q-H, power consumption, and efficiency curves shall be submitted. Standards: EN 809 or equivalent for pump safety; IEC 60034 series or equivalent for the motor. Hydraulic testing and tolerances according to ISO 9906 (Class 2B or Class 1B). Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [130-132] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 2 |  | 45000 | Frequency converter 130 -132 kW | 9000
| 2.4 | Sewage pump Q= 500 m³/h, H=30-40m | Application: Municipal sewage pumping stations (KNS) for untreated or partially screened wastewater containing faecal matter, suspended, fibrous solids, and abrasive sand/grit.2 Pump type: Horizontal centrifugal sewage pump for dry-pit/dry-well installation, mounted on a common steel or cast iron baseframe. Installation: Dry installation outside the pumped liquid. Back Pull-Out design or equivalent allowing rotating element maintenance without disconnecting the casing from pipework. Operating point: As specified in the Schedule of Requirements Pump design: Non-clog sewage pump suitable for reliable operation with municipal wastewater Impeller: Single-channel, multi-channel, or equivalent non-clog design with hydraulic efficiency minimum 78-80% at BEP. Dynamically balanced. Free passage: Minimum 80 mm (or minimum 100 mm for capacities up to 500 m³/h). Liquid temperature: Maximum liquid temperature: minimum +40 °C. Pump materials: Wear-resistant cast iron (minimum EN-GJS-400 or equivalent wear-resistant alloy). Grey cast iron configurations must include replaceable wear components. Wear Protection: Replaceable wear rings or wear plates on the casing and/or impeller side. Shaft: Stainless steel (minimum AISI 431 or manufacturer's equivalent grade protected by a shaft sleeve). Mechanical seal:Double mechanical shaft seal operating in an oil chamber. Seal face materials on the liquid side shall be Silicon Carbide (SiC/SiC) or Tungsten Carbide. Oil chamber equipped with a leakage sensor. Bearings: Heavy-duty grease or oil-lubricated bearings with minimum L10 bearing life of 50,000 hours. Motor type: Three-phase squirrel-cage induction motor. Electrical data: Rated voltage: 400 V ±10 %. Rated frequency: 50 Hz. Motor efficiency: IE3 minimum according to IEC 60034-30-1. Insulation class: Class F minimum. Degree of protection: IP55-IP57 according to IEC 60034-5. If an IP68 motor is offered, it must include an integrated cooling jacket for continuous dry-run operation. Duty:Continuous duty, S1. Pump efficiency: Supplier shall declare hydraulic efficiency at the duty point. The duty point shall lie within the manufacturer's preferred operating range (close to BEP). Performance curve: Manufacturer's official Q-H, power consumption, and efficiency curves shall be submitted. Standards: EN 809 or equivalent for pump safety; IEC 60034 series or equivalent for the motor. Hydraulic testing and tolerances according to ISO 9906 (Class 2B or Class 1B). Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [130-132] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 18 |  | 25000 | Frequency converter 90 -110 kW | 6100
| 2.5 | Sewage pump Q= 500 m³/h, H=70-80m | Application: Municipal sewage pumping stations (KNS) for untreated or partially screened wastewater containing faecal matter, suspended, fibrous solids, and abrasive sand/grit.2 Pump type: Horizontal centrifugal sewage pump for dry-pit/dry-well installation, mounted on a common steel or cast iron baseframe. Installation: Dry installation outside the pumped liquid. Back Pull-Out design or equivalent allowing rotating element maintenance without disconnecting the casing from pipework. Operating point: As specified in the Schedule of Requirements Pump design: Non-clog sewage pump suitable for reliable operation with municipal wastewater Impeller: Single-channel, multi-channel, or equivalent non-clog design with hydraulic efficiency minimum 78-80% at BEP. Dynamically balanced. Free passage: Minimum 80 mm (or minimum 100 mm for capacities up to 500 m³/h). Liquid temperature: Maximum liquid temperature: minimum +40 °C. Pump materials: Wear-resistant cast iron (minimum EN-GJS-400 or equivalent wear-resistant alloy). Grey cast iron configurations must include replaceable wear components. Wear Protection: Replaceable wear rings or wear plates on the casing and/or impeller side. Shaft: Stainless steel (minimum AISI 431 or manufacturer's equivalent grade protected by a shaft sleeve). Mechanical seal:Double mechanical shaft seal operating in an oil chamber. Seal face materials on the liquid side shall be Silicon Carbide (SiC/SiC) or Tungsten Carbide. Oil chamber equipped with a leakage sensor. Bearings: Heavy-duty grease or oil-lubricated bearings with minimum L10 bearing life of 50,000 hours. Motor type: Three-phase squirrel-cage induction motor. Electrical data: Rated voltage: 400 V ±10 %. Rated frequency: 50 Hz. Motor efficiency: IE3 minimum according to IEC 60034-30-1. Insulation class: Class F minimum. Degree of protection: IP55-IP57 according to IEC 60034-5. If an IP68 motor is offered, it must include an integrated cooling jacket for continuous dry-run operation. Duty:Continuous duty, S1. Pump efficiency: Supplier shall declare hydraulic efficiency at the duty point. The duty point shall lie within the manufacturer's preferred operating range (close to BEP). Performance curve: Manufacturer's official Q-H, power consumption, and efficiency curves shall be submitted. Standards: EN 809 or equivalent for pump safety; IEC 60034 series or equivalent for the motor. Hydraulic testing and tolerances according to ISO 9906 (Class 2B or Class 1B). Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [130-132] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 4 |  | 40000 | Frequency converter 160 -180 kW | 18500
3 | 3.1 | Water supply pump, Q = 250 m³/h, H = 30–50 m | Application: Pumping of clean, treated or raw water in municipal water supply systems Pump type: Horizontal centrifugal pump for dry installation, long-coupled, suitable for continuous-duty water supply applications Operating range: The pump shall be suitable for variable-speed operation by means of a frequency converter Pump casing: Cast iron or ductile iron suitable for water service, or equivalent material with documented mechanical and corrosion resistance Impeller:Must be made of Ductile Iron EN-GJS-400-15 (EN 1563) or Stainless Steel EN 1.4301 (ISO 15510), or equivalent, strictly suitable for the pumped water properties. The impeller must be dynamically balanced in accordance with ISO 21940-11 (balance quality grade G2.5 or better. Shaft: High-strength stainless steel EN 1.4021 or EN 1.4401 (ISO 15510), or equivalent, corrosion-resistant Mechanical seal : The pump must be equipped with a balanced mechanical seal in accordance with EN 12756, featuring SiC/Carbon (or SiC/SiC) faces, EPDM elastomers, and AISI 316 stainless steel metal parts, or equivalent Bearings: Heavy-duty rolling bearings suitable for continuous 24/7 operation. The minimum calculated bearing operating life (L10h) must be at least 25,000 hours under maximum dynamic loads in accordance with ISO 281. Coupling: Torsionally flexible coupling with a spacer element (Spacer Coupling) to allow the "Back Pull-Out" maintenance method without dismantling the motor or piping, or equivalent. Equipped with a robust coupling guard according to EN ISO 13857. Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [45-50] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 10 |  | 8000 | Frequency converter 45 - 50 kW | 4000 | 0
| 3.2 | Water supply pump, Q = 250 m³/h, H = 50–75 m | Application: Pumping of clean, treated or raw water in municipal water supply systems Pump type: Horizontal centrifugal pump for dry installation, long-coupled, suitable for continuous-duty water supply applications Operating range: The pump shall be suitable for variable-speed operation by means of a frequency converter Pump casing: Cast iron or ductile iron suitable for water service, or equivalent material with documented mechanical and corrosion resistance Impeller:Must be made of Ductile Iron EN-GJS-400-15 (EN 1563) or Stainless Steel EN 1.4301 (ISO 15510), or equivalent, strictly suitable for the pumped water properties. The impeller must be dynamically balanced in accordance with ISO 21940-11 (balance quality grade G2.5 or better. Shaft: High-strength stainless steel EN 1.4021 or EN 1.4401 (ISO 15510), or equivalent, corrosion-resistant Mechanical seal : The pump must be equipped with a balanced mechanical seal in accordance with EN 12756, featuring SiC/Carbon (or SiC/SiC) faces, EPDM elastomers, and AISI 316 stainless steel metal parts, or equivalent Bearings: Heavy-duty rolling bearings suitable for continuous 24/7 operation. The minimum calculated bearing operating life (L10h) must be at least 25,000 hours under maximum dynamic loads in accordance with ISO 281. Coupling: Torsionally flexible coupling with a spacer element (Spacer Coupling) to allow the "Back Pull-Out" maintenance method without dismantling the motor or piping, or equivalent. Equipped with a robust coupling guard according to EN ISO 13857. Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [45-50] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 14 |  | 12000 | Frequency converter 75 - 80 kW | 5800
| 3.3 | Water supply pump, Q = 250 m³/h, H =75-100 m | Application: Pumping of clean, treated or raw water in municipal water supply systems Pump type: Horizontal centrifugal pump for dry installation, long-coupled, suitable for continuous-duty water supply applications Operating range: The pump shall be suitable for variable-speed operation by means of a frequency converter Pump casing: Cast iron or ductile iron suitable for water service, or equivalent material with documented mechanical and corrosion resistance Impeller:Must be made of Ductile Iron EN-GJS-400-15 (EN 1563) or Stainless Steel EN 1.4301 (ISO 15510), or equivalent, strictly suitable for the pumped water properties. The impeller must be dynamically balanced in accordance with ISO 21940-11 (balance quality grade G2.5 or better. Shaft: High-strength stainless steel EN 1.4021 or EN 1.4401 (ISO 15510), or equivalent, corrosion-resistant Mechanical seal : The pump must be equipped with a balanced mechanical seal in accordance with EN 12756, featuring SiC/Carbon (or SiC/SiC) faces, EPDM elastomers, and AISI 316 stainless steel metal parts, or equivalent Bearings: Heavy-duty rolling bearings suitable for continuous 24/7 operation. The minimum calculated bearing operating life (L10h) must be at least 25,000 hours under maximum dynamic loads in accordance with ISO 281. Coupling: Torsionally flexible coupling with a spacer element (Spacer Coupling) to allow the "Back Pull-Out" maintenance method without dismantling the motor or piping, or equivalent. Equipped with a robust coupling guard according to EN ISO 13857. Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [45-50] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 10 |  | 20000 | Frequency converter 90 -110 kW | 6100

## Scpecification Lots 4,5,6
Lot | Position | Item description |  | Quantity [pcs.] | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns B-E, please indicate "Yes". Otherwise, describe your special features in this column. | Unit cost, EUR |  | Control Panel Unit cost, EUR
all lots |  | General requirement | Availability of an authorized service center in Ukraine. In the event of a warranty case, the center must resolve the issue within 60 days from the date of application.
4 | 4.1 | Flanged gate valve, DN400 | FLANGED RESILIENT-SEATED WEDGE GATE VALVE – PN10 For potable water, raw water and treated wastewater Application:Potable water, raw water and treated wastewater/effluent with low content of suspended solids and fibrous impurities. Pressure rating:PN10. Valve type:Flanged resilient-seated wedge gate valve for isolation service. Body and bonnet:Ductile iron or equivalent material suitable for PN10 service conditions. Wedge:Ductile iron wedge, fully encapsulated/vulcanized with EPDM or equivalent elastomer suitable for the specified operating medium. Elastomer shall be suitable for potable-water applications where applicable. Stem:Non-rising stem made of stainless steel or equivalent corrosion-resistant material. Stem sealing:Reliable sealing system suitable for the specified pressure, temperature and operating medium. Bolting:Corrosion-resistant material suitable for the service conditions. Corrosion protection:Factory-applied fusion-bonded epoxy or equivalent heavy-duty corrosion-protection system suitable for buried and/or external installation. Coating shall comply with EN 14901-1 or an equivalent recognized standard. Flanged connection:Flanged ends according to EN 1092-2, PN10. Face-to-face dimensions:According to EN 558, Series 14 (F4). Design and performance:EN 1074-1 and EN 1074-2; EN 1171 where applicable. Seat tightness:The closed valve shall provide tight shut-off in accordance with the applicable requirements of EN 12266-1, with no visible leakage under the specified test conditions. Operating temperature:Suitable for the specified water/wastewater service, approximately 0 °C to +70 °C. Operating conditions:The valve shall be capable of safe opening and closing at the specified operating pressure and the maximum differential pressure declared by the manufacturer. Operating torque:The manufacturer shall declare the maximum operating torque and, where applicable, the torque required for gearbox or actuator selection. Actuation:Handwheel for manual operation as standard. The valve shall be suitable for installation of a gearbox or electric actuator where required. Installation:The valve shall be supplied complete and suitable for installation in accordance with the manufacturer's standard installation requirements. Potable-water compliance:Where used in potable-water systems, all materials, elastomers and coatings in contact with drinking water shall comply with applicable national/EU requirements. Recognized drinking-water approval or equivalent conformity may be provided. | 35 |  | 2800
| 4.2 | Flanged gate valve, DN500 | FLANGED RESILIENT-SEATED WEDGE GATE VALVE – PN10 For potable water, raw water and treated wastewater Application:Potable water, raw water and treated wastewater/effluent with low content of suspended solids and fibrous impurities. Pressure rating:PN10. Valve type:Flanged resilient-seated wedge gate valve for isolation service. Body and bonnet:Ductile iron or equivalent material suitable for PN10 service conditions. Wedge:Ductile iron wedge, fully encapsulated/vulcanized with EPDM or equivalent elastomer suitable for the specified operating medium. Elastomer shall be suitable for potable-water applications where applicable. Stem:Non-rising stem made of stainless steel or equivalent corrosion-resistant material. Stem sealing:Reliable sealing system suitable for the specified pressure, temperature and operating medium. Bolting:Corrosion-resistant material suitable for the service conditions. Corrosion protection:Factory-applied fusion-bonded epoxy or equivalent heavy-duty corrosion-protection system suitable for buried and/or external installation. Coating shall comply with EN 14901-1 or an equivalent recognized standard. Flanged connection:Flanged ends according to EN 1092-2, PN10. Face-to-face dimensions:According to EN 558, Series 14 (F4). Design and performance:EN 1074-1 and EN 1074-2; EN 1171 where applicable. Seat tightness:The closed valve shall provide tight shut-off in accordance with the applicable requirements of EN 12266-1, with no visible leakage under the specified test conditions. Operating temperature:Suitable for the specified water/wastewater service, approximately 0 °C to +70 °C. Operating conditions:The valve shall be capable of safe opening and closing at the specified operating pressure and the maximum differential pressure declared by the manufacturer. Operating torque:The manufacturer shall declare the maximum operating torque and, where applicable, the torque required for gearbox or actuator selection. Actuation:Handwheel for manual operation as standard. The valve shall be suitable for installation of a gearbox or electric actuator where required. Installation:The valve shall be supplied complete and suitable for installation in accordance with the manufacturer's standard installation requirements. Potable-water compliance:Where used in potable-water systems, all materials, elastomers and coatings in contact with drinking water shall comply with applicable national/EU requirements. Recognized drinking-water approval or equivalent conformity may be provided. | 8 |  | 4300
| 4.3 | Flanged gate valve, DN600 | FLANGED RESILIENT-SEATED WEDGE GATE VALVE – PN10 For potable water, raw water and treated wastewater Application:Potable water, raw water and treated wastewater/effluent with low content of suspended solids and fibrous impurities. Pressure rating:PN10. Valve type:Flanged resilient-seated wedge gate valve for isolation service. Body and bonnet:Ductile iron or equivalent material suitable for PN10 service conditions. Wedge:Ductile iron wedge, fully encapsulated/vulcanized with EPDM or equivalent elastomer suitable for the specified operating medium. Elastomer shall be suitable for potable-water applications where applicable. Stem:Non-rising stem made of stainless steel or equivalent corrosion-resistant material. Stem sealing:Reliable sealing system suitable for the specified pressure, temperature and operating medium. Bolting:Corrosion-resistant material suitable for the service conditions. Corrosion protection:Factory-applied fusion-bonded epoxy or equivalent heavy-duty corrosion-protection system suitable for buried and/or external installation. Coating shall comply with EN 14901-1 or an equivalent recognized standard. Flanged connection:Flanged ends according to EN 1092-2, PN10. Face-to-face dimensions:According to EN 558, Series 14 (F4). Design and performance:EN 1074-1 and EN 1074-2; EN 1171 where applicable. Seat tightness:The closed valve shall provide tight shut-off in accordance with the applicable requirements of EN 12266-1, with no visible leakage under the specified test conditions. Operating temperature:Suitable for the specified water/wastewater service, approximately 0 °C to +70 °C. Operating conditions:The valve shall be capable of safe opening and closing at the specified operating pressure and the maximum differential pressure declared by the manufacturer. Operating torque:The manufacturer shall declare the maximum operating torque and, where applicable, the torque required for gearbox or actuator selection. Actuation:Handwheel for manual operation as standard. The valve shall be suitable for installation of a gearbox or electric actuator where required. Installation:The valve shall be supplied complete and suitable for installation in accordance with the manufacturer's standard installation requirements. Potable-water compliance:Where used in potable-water systems, all materials, elastomers and coatings in contact with drinking water shall comply with applicable national/EU requirements. Recognized drinking-water approval or equivalent conformity may be provided. | 45 |  | 6500 |  |  | #REF!
| 1.4 | Flanged gate valve, DN400 | FLANGED RESILIENT-SEATED WEDGE GATE VALVE – PN16 For potable water supply systems Application:Potable water supply and distribution systems. Pressure rating:PN16. Valve type:Flanged resilient-seated wedge gate valve for isolation service. Body and bonnet:Ductile iron or equivalent material suitable for PN16 potable-water service conditions. Wedge:Ductile iron wedge, fully encapsulated/vulcanized with EPDM or equivalent elastomer suitable for potable water. Stem:Non-rising stem made of stainless steel or equivalent corrosion-resistant material. Stem sealing:Reliable sealing system suitable for PN16 potable-water service. Bolting:Corrosion-resistant material suitable for the service conditions. Corrosion protection:Factory-applied fusion-bonded epoxy or equivalent heavy-duty corrosion-protection system suitable for buried and/or external installation. Coating shall comply with EN 14901-1 or an equivalent recognized standard. Flanged connection:Flanged ends according to EN 1092-2, PN16. Face-to-face dimensions:According to EN 558, Series 14 (F4). Design and performance:EN 1074-1 and EN 1074-2; EN 1171 where applicable. Testing:Production testing according to EN 12266-1 or equivalent recognized standard. The closed valve shall provide tight shut-off in accordance with the applicable requirements of EN 12266-1, with no visible leakage under the specified test conditions. Operating temperature:Suitable for potable-water service, approximately 0 °C to +70 °C. Operating conditions:The valve shall be capable of safe opening and closing at PN16 and at the maximum differential pressure declared by the manufacturer. Operating torque:The manufacturer shall declare the maximum operating torque and, where applicable, the torque required for gearbox or actuator selection. Actuation:Handwheel for manual operation as standard. The valve shall be suitable for installation of a gearbox or electric actuator where required. Installation:Suitable for installation in valve chambers Potable-water compliance:All wetted materials, elastomers and coatings shall comply with applicable requirements for potable-water contact. Recognized drinking-water approval/certification such as WRAS, ACS, DVGW, KIWA, SVGW, Belgaqua or equivalent nationally/internationally recognized conformity shall be accepted. | 4 |  | 2700
| 4.5 | Flanged gate valve, DN500 | FLANGED RESILIENT-SEATED WEDGE GATE VALVE – PN16 For potable water supply systems Application:Potable water supply and distribution systems. Pressure rating:PN16. Valve type:Flanged resilient-seated wedge gate valve for isolation service. Body and bonnet:Ductile iron or equivalent material suitable for PN16 potable-water service conditions. Wedge:Ductile iron wedge, fully encapsulated/vulcanized with EPDM or equivalent elastomer suitable for potable water. Stem:Non-rising stem made of stainless steel or equivalent corrosion-resistant material. Stem sealing:Reliable sealing system suitable for PN16 potable-water service. Bolting:Corrosion-resistant material suitable for the service conditions. Corrosion protection:Factory-applied fusion-bonded epoxy or equivalent heavy-duty corrosion-protection system suitable for buried and/or external installation. Coating shall comply with EN 14901-1 or an equivalent recognized standard. Flanged connection:Flanged ends according to EN 1092-2, PN16. Face-to-face dimensions:According to EN 558, Series 14 (F4). Design and performance:EN 1074-1 and EN 1074-2; EN 1171 where applicable. Testing:Production testing according to EN 12266-1 or equivalent recognized standard. The closed valve shall provide tight shut-off in accordance with the applicable requirements of EN 12266-1, with no visible leakage under the specified test conditions. Operating temperature:Suitable for potable-water service, approximately 0 °C to +70 °C. Operating conditions:The valve shall be capable of safe opening and closing at PN16 and at the maximum differential pressure declared by the manufacturer. Operating torque:The manufacturer shall declare the maximum operating torque and, where applicable, the torque required for gearbox or actuator selection. Actuation:Handwheel for manual operation as standard. The valve shall be suitable for installation of a gearbox or electric actuator where required. Installation:Suitable for installation in valve chambers Potable-water compliance:All wetted materials, elastomers and coatings shall comply with applicable requirements for potable-water contact. Recognized drinking-water approval/certification such as WRAS, ACS, DVGW, KIWA, SVGW, Belgaqua or equivalent nationally/internationally recognized conformity shall be accepted. | 2 |  | 4300
| 4.6 | Flanged gate valve, DN600 | FLANGED RESILIENT-SEATED WEDGE GATE VALVE – PN16 For potable water supply systems Application:Potable water supply and distribution systems. Pressure rating:PN16. Valve type:Flanged resilient-seated wedge gate valve for isolation service. Body and bonnet:Ductile iron or equivalent material suitable for PN16 potable-water service conditions. Wedge:Ductile iron wedge, fully encapsulated/vulcanized with EPDM or equivalent elastomer suitable for potable water. Stem:Non-rising stem made of stainless steel or equivalent corrosion-resistant material. Stem sealing:Reliable sealing system suitable for PN16 potable-water service. Bolting:Corrosion-resistant material suitable for the service conditions. Corrosion protection:Factory-applied fusion-bonded epoxy or equivalent heavy-duty corrosion-protection system suitable for buried and/or external installation. Coating shall comply with EN 14901-1 or an equivalent recognized standard. Flanged connection:Flanged ends according to EN 1092-2, PN16. Face-to-face dimensions:According to EN 558, Series 14 (F4). Design and performance:EN 1074-1 and EN 1074-2; EN 1171 where applicable. Testing:Production testing according to EN 12266-1 or equivalent recognized standard. The closed valve shall provide tight shut-off in accordance with the applicable requirements of EN 12266-1, with no visible leakage under the specified test conditions. Operating temperature:Suitable for potable-water service, approximately 0 °C to +70 °C. Operating conditions:The valve shall be capable of safe opening and closing at PN16 and at the maximum differential pressure declared by the manufacturer. Operating torque:The manufacturer shall declare the maximum operating torque and, where applicable, the torque required for gearbox or actuator selection. Actuation:Handwheel for manual operation as standard. The valve shall be suitable for installation of a gearbox or electric actuator where required. Installation:Suitable for installation in valve chambers Potable-water compliance:All wetted materials, elastomers and coatings shall comply with applicable requirements for potable-water contact. Recognized drinking-water approval/certification such as WRAS, ACS, DVGW, KIWA, SVGW, Belgaqua or equivalent nationally/internationally recognized conformity shall be accepted. | 10 |  | 6600 |  |  | #REF! | #REF!
5 | 5.1 | Sewage pump Q= 250 m³/h, H=30-40m | Application: Municipal sewage pumping stations (KNS) for untreated or partially screened wastewater containing faecal matter, suspended, fibrous solids, and abrasive sand/grit.2 Pump type: Horizontal centrifugal sewage pump for dry-pit/dry-well installation, mounted on a common steel or cast iron baseframe. Installation: Dry installation outside the pumped liquid. Back Pull-Out design or equivalent allowing rotating element maintenance without disconnecting the casing from pipework. Operating point: As specified in the Schedule of Requirements Pump design: Non-clog sewage pump suitable for reliable operation with municipal wastewater Impeller: Single-channel, multi-channel, or equivalent non-clog design with hydraulic efficiency minimum 78-80% at BEP. Dynamically balanced. Free passage: Minimum 80 mm (or minimum 100 mm for capacities up to 500 m³/h). Liquid temperature: Maximum liquid temperature: minimum +40 °C. Pump materials: Wear-resistant cast iron (minimum EN-GJS-400 or equivalent wear-resistant alloy). Grey cast iron configurations must include replaceable wear components. Wear Protection: Replaceable wear rings or wear plates on the casing and/or impeller side. Shaft: Stainless steel (minimum AISI 431 or manufacturer's equivalent grade protected by a shaft sleeve). Mechanical seal:Double mechanical shaft seal operating in an oil chamber. Seal face materials on the liquid side shall be Silicon Carbide (SiC/SiC) or Tungsten Carbide. Oil chamber equipped with a leakage sensor. Bearings: Heavy-duty grease or oil-lubricated bearings with minimum L10 bearing life of 50,000 hours. Motor type: Three-phase squirrel-cage induction motor. Electrical data: Rated voltage: 400 V ±10 %. Rated frequency: 50 Hz. Motor efficiency: IE3 minimum according to IEC 60034-30-1. Insulation class: Class F minimum. Degree of protection: IP55-IP57 according to IEC 60034-5. If an IP68 motor is offered, it must include an integrated cooling jacket for continuous dry-run operation. Duty:Continuous duty, S1. Pump efficiency: Supplier shall declare hydraulic efficiency at the duty point. The duty point shall lie within the manufacturer's preferred operating range (close to BEP). Performance curve: Manufacturer's official Q-H, power consumption, and efficiency curves shall be submitted. Standards: EN 809 or equivalent for pump safety; IEC 60034 series or equivalent for the motor. Hydraulic testing and tolerances according to ISO 9906 (Class 2B or Class 1B). Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [45-50] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip). | 10 |  | 15000 | Frequency converter 45 - 50 kW | 3900
| 5.2 | Sewage pump Q= 250 m³/h, H=50-60m | Application: Municipal sewage pumping stations (KNS) for untreated or partially screened wastewater containing faecal matter, suspended, fibrous solids, and abrasive sand/grit.2 Pump type: Horizontal centrifugal sewage pump for dry-pit/dry-well installation, mounted on a common steel or cast iron baseframe. Installation: Dry installation outside the pumped liquid. Back Pull-Out design or equivalent allowing rotating element maintenance without disconnecting the casing from pipework. Operating point: As specified in the Schedule of Requirements Pump design: Non-clog sewage pump suitable for reliable operation with municipal wastewater Impeller: Single-channel, multi-channel, or equivalent non-clog design with hydraulic efficiency minimum 78-80% at BEP. Dynamically balanced. Free passage: Minimum 80 mm (or minimum 100 mm for capacities up to 500 m³/h). Liquid temperature: Maximum liquid temperature: minimum +40 °C. Pump materials: Wear-resistant cast iron (minimum EN-GJS-400 or equivalent wear-resistant alloy). Grey cast iron configurations must include replaceable wear components. Wear Protection: Replaceable wear rings or wear plates on the casing and/or impeller side. Shaft: Stainless steel (minimum AISI 431 or manufacturer's equivalent grade protected by a shaft sleeve). Mechanical seal:Double mechanical shaft seal operating in an oil chamber. Seal face materials on the liquid side shall be Silicon Carbide (SiC/SiC) or Tungsten Carbide. Oil chamber equipped with a leakage sensor. Bearings: Heavy-duty grease or oil-lubricated bearings with minimum L10 bearing life of 50,000 hours. Motor type: Three-phase squirrel-cage induction motor. Electrical data: Rated voltage: 400 V ±10 %. Rated frequency: 50 Hz. Motor efficiency: IE3 minimum according to IEC 60034-30-1. Insulation class: Class F minimum. Degree of protection: IP55-IP57 according to IEC 60034-5. If an IP68 motor is offered, it must include an integrated cooling jacket for continuous dry-run operation. Duty:Continuous duty, S1. Pump efficiency: Supplier shall declare hydraulic efficiency at the duty point. The duty point shall lie within the manufacturer's preferred operating range (close to BEP). Performance curve: Manufacturer's official Q-H, power consumption, and efficiency curves shall be submitted. Standards: EN 809 or equivalent for pump safety; IEC 60034 series or equivalent for the motor. Hydraulic testing and tolerances according to ISO 9906 (Class 2B or Class 1B). Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [75-80] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 6 |  | 22000 | Frequency converter 75 - 80 kW | 5800
| 5.3 | Sewage pump Q= 250 m³/h, H=90-100m | Application: Municipal sewage pumping stations (KNS) for untreated or partially screened wastewater containing faecal matter, suspended, fibrous solids, and abrasive sand/grit.2 Pump type: Horizontal centrifugal sewage pump for dry-pit/dry-well installation, mounted on a common steel or cast iron baseframe. Installation: Dry installation outside the pumped liquid. Back Pull-Out design or equivalent allowing rotating element maintenance without disconnecting the casing from pipework. Operating point: As specified in the Schedule of Requirements Pump design: Non-clog sewage pump suitable for reliable operation with municipal wastewater Impeller: Single-channel, multi-channel, or equivalent non-clog design with hydraulic efficiency minimum 78-80% at BEP. Dynamically balanced. Free passage: Minimum 80 mm (or minimum 100 mm for capacities up to 500 m³/h). Liquid temperature: Maximum liquid temperature: minimum +40 °C. Pump materials: Wear-resistant cast iron (minimum EN-GJS-400 or equivalent wear-resistant alloy). Grey cast iron configurations must include replaceable wear components. Wear Protection: Replaceable wear rings or wear plates on the casing and/or impeller side. Shaft: Stainless steel (minimum AISI 431 or manufacturer's equivalent grade protected by a shaft sleeve). Mechanical seal:Double mechanical shaft seal operating in an oil chamber. Seal face materials on the liquid side shall be Silicon Carbide (SiC/SiC) or Tungsten Carbide. Oil chamber equipped with a leakage sensor. Bearings: Heavy-duty grease or oil-lubricated bearings with minimum L10 bearing life of 50,000 hours. Motor type: Three-phase squirrel-cage induction motor. Electrical data: Rated voltage: 400 V ±10 %. Rated frequency: 50 Hz. Motor efficiency: IE3 minimum according to IEC 60034-30-1. Insulation class: Class F minimum. Degree of protection: IP55-IP57 according to IEC 60034-5. If an IP68 motor is offered, it must include an integrated cooling jacket for continuous dry-run operation. Duty:Continuous duty, S1. Pump efficiency: Supplier shall declare hydraulic efficiency at the duty point. The duty point shall lie within the manufacturer's preferred operating range (close to BEP). Performance curve: Manufacturer's official Q-H, power consumption, and efficiency curves shall be submitted. Standards: EN 809 or equivalent for pump safety; IEC 60034 series or equivalent for the motor. Hydraulic testing and tolerances according to ISO 9906 (Class 2B or Class 1B). Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [130-132] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 2 |  | 45000 | Frequency converter 130 -132 kW | 9000
| 5.4 | Sewage pump Q= 500 m³/h, H=30-40m | Application: Municipal sewage pumping stations (KNS) for untreated or partially screened wastewater containing faecal matter, suspended, fibrous solids, and abrasive sand/grit.2 Pump type: Horizontal centrifugal sewage pump for dry-pit/dry-well installation, mounted on a common steel or cast iron baseframe. Installation: Dry installation outside the pumped liquid. Back Pull-Out design or equivalent allowing rotating element maintenance without disconnecting the casing from pipework. Operating point: As specified in the Schedule of Requirements Pump design: Non-clog sewage pump suitable for reliable operation with municipal wastewater Impeller: Single-channel, multi-channel, or equivalent non-clog design with hydraulic efficiency minimum 78-80% at BEP. Dynamically balanced. Free passage: Minimum 80 mm (or minimum 100 mm for capacities up to 500 m³/h). Liquid temperature: Maximum liquid temperature: minimum +40 °C. Pump materials: Wear-resistant cast iron (minimum EN-GJS-400 or equivalent wear-resistant alloy). Grey cast iron configurations must include replaceable wear components. Wear Protection: Replaceable wear rings or wear plates on the casing and/or impeller side. Shaft: Stainless steel (minimum AISI 431 or manufacturer's equivalent grade protected by a shaft sleeve). Mechanical seal:Double mechanical shaft seal operating in an oil chamber. Seal face materials on the liquid side shall be Silicon Carbide (SiC/SiC) or Tungsten Carbide. Oil chamber equipped with a leakage sensor. Bearings: Heavy-duty grease or oil-lubricated bearings with minimum L10 bearing life of 50,000 hours. Motor type: Three-phase squirrel-cage induction motor. Electrical data: Rated voltage: 400 V ±10 %. Rated frequency: 50 Hz. Motor efficiency: IE3 minimum according to IEC 60034-30-1. Insulation class: Class F minimum. Degree of protection: IP55-IP57 according to IEC 60034-5. If an IP68 motor is offered, it must include an integrated cooling jacket for continuous dry-run operation. Duty:Continuous duty, S1. Pump efficiency: Supplier shall declare hydraulic efficiency at the duty point. The duty point shall lie within the manufacturer's preferred operating range (close to BEP). Performance curve: Manufacturer's official Q-H, power consumption, and efficiency curves shall be submitted. Standards: EN 809 or equivalent for pump safety; IEC 60034 series or equivalent for the motor. Hydraulic testing and tolerances according to ISO 9906 (Class 2B or Class 1B). Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [130-132] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 10 |  | 25000 | Frequency converter 90 -110 kW | 6100
| 5.5 | Sewage pump Q= 500 m³/h, H=70-80m | Application: Municipal sewage pumping stations (KNS) for untreated or partially screened wastewater containing faecal matter, suspended, fibrous solids, and abrasive sand/grit.2 Pump type: Horizontal centrifugal sewage pump for dry-pit/dry-well installation, mounted on a common steel or cast iron baseframe. Installation: Dry installation outside the pumped liquid. Back Pull-Out design or equivalent allowing rotating element maintenance without disconnecting the casing from pipework. Operating point: As specified in the Schedule of Requirements Pump design: Non-clog sewage pump suitable for reliable operation with municipal wastewater Impeller: Single-channel, multi-channel, or equivalent non-clog design with hydraulic efficiency minimum 78-80% at BEP. Dynamically balanced. Free passage: Minimum 80 mm (or minimum 100 mm for capacities up to 500 m³/h). Liquid temperature: Maximum liquid temperature: minimum +40 °C. Pump materials: Wear-resistant cast iron (minimum EN-GJS-400 or equivalent wear-resistant alloy). Grey cast iron configurations must include replaceable wear components. Wear Protection: Replaceable wear rings or wear plates on the casing and/or impeller side. Shaft: Stainless steel (minimum AISI 431 or manufacturer's equivalent grade protected by a shaft sleeve). Mechanical seal:Double mechanical shaft seal operating in an oil chamber. Seal face materials on the liquid side shall be Silicon Carbide (SiC/SiC) or Tungsten Carbide. Oil chamber equipped with a leakage sensor. Bearings: Heavy-duty grease or oil-lubricated bearings with minimum L10 bearing life of 50,000 hours. Motor type: Three-phase squirrel-cage induction motor. Electrical data: Rated voltage: 400 V ±10 %. Rated frequency: 50 Hz. Motor efficiency: IE3 minimum according to IEC 60034-30-1. Insulation class: Class F minimum. Degree of protection: IP55-IP57 according to IEC 60034-5. If an IP68 motor is offered, it must include an integrated cooling jacket for continuous dry-run operation. Duty:Continuous duty, S1. Pump efficiency: Supplier shall declare hydraulic efficiency at the duty point. The duty point shall lie within the manufacturer's preferred operating range (close to BEP). Performance curve: Manufacturer's official Q-H, power consumption, and efficiency curves shall be submitted. Standards: EN 809 or equivalent for pump safety; IEC 60034 series or equivalent for the motor. Hydraulic testing and tolerances according to ISO 9906 (Class 2B or Class 1B). Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [130-132] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 2 |  | 40000 | Frequency converter 160 -180 kW | 18500
6 | 6.1 | Water supply pump, Q = 250 m³/h, H = 30–50 m | Application: Pumping of clean, treated or raw water in municipal water supply systems Pump type: Horizontal centrifugal pump for dry installation, long-coupled, suitable for continuous-duty water supply applications Operating range: The pump shall be suitable for variable-speed operation by means of a frequency converter Pump casing: Cast iron or ductile iron suitable for water service, or equivalent material with documented mechanical and corrosion resistance Impeller:Must be made of Ductile Iron EN-GJS-400-15 (EN 1563) or Stainless Steel EN 1.4301 (ISO 15510), or equivalent, strictly suitable for the pumped water properties. The impeller must be dynamically balanced in accordance with ISO 21940-11 (balance quality grade G2.5 or better. Shaft: High-strength stainless steel EN 1.4021 or EN 1.4401 (ISO 15510), or equivalent, corrosion-resistant Mechanical seal : The pump must be equipped with a balanced mechanical seal in accordance with EN 12756, featuring SiC/Carbon (or SiC/SiC) faces, EPDM elastomers, and AISI 316 stainless steel metal parts, or equivalent Bearings: Heavy-duty rolling bearings suitable for continuous 24/7 operation. The minimum calculated bearing operating life (L10h) must be at least 25,000 hours under maximum dynamic loads in accordance with ISO 281. Coupling: Torsionally flexible coupling with a spacer element (Spacer Coupling) to allow the "Back Pull-Out" maintenance method without dismantling the motor or piping, or equivalent. Equipped with a robust coupling guard according to EN ISO 13857. Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [45-50] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 4 |  | 8000 | Frequency converter 45 - 50 kW | 4000 | 0
| 6.2 | Water supply pump, Q = 250 m³/h, H = 50–75 m | Application: Pumping of clean, treated or raw water in municipal water supply systems Pump type: Horizontal centrifugal pump for dry installation, long-coupled, suitable for continuous-duty water supply applications Operating range: The pump shall be suitable for variable-speed operation by means of a frequency converter Pump casing: Cast iron or ductile iron suitable for water service, or equivalent material with documented mechanical and corrosion resistance Impeller:Must be made of Ductile Iron EN-GJS-400-15 (EN 1563) or Stainless Steel EN 1.4301 (ISO 15510), or equivalent, strictly suitable for the pumped water properties. The impeller must be dynamically balanced in accordance with ISO 21940-11 (balance quality grade G2.5 or better. Shaft: High-strength stainless steel EN 1.4021 or EN 1.4401 (ISO 15510), or equivalent, corrosion-resistant Mechanical seal : The pump must be equipped with a balanced mechanical seal in accordance with EN 12756, featuring SiC/Carbon (or SiC/SiC) faces, EPDM elastomers, and AISI 316 stainless steel metal parts, or equivalent Bearings: Heavy-duty rolling bearings suitable for continuous 24/7 operation. The minimum calculated bearing operating life (L10h) must be at least 25,000 hours under maximum dynamic loads in accordance with ISO 281. Coupling: Torsionally flexible coupling with a spacer element (Spacer Coupling) to allow the "Back Pull-Out" maintenance method without dismantling the motor or piping, or equivalent. Equipped with a robust coupling guard according to EN ISO 13857. Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [45-50] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 7 |  | 12000 | Frequency converter 75 - 80 kW | 5800
| 6.3 | Water supply pump, Q = 250 m³/h, H =75-100 m | Application: Pumping of clean, treated or raw water in municipal water supply systems Pump type: Horizontal centrifugal pump for dry installation, long-coupled, suitable for continuous-duty water supply applications Operating range: The pump shall be suitable for variable-speed operation by means of a frequency converter Pump casing: Cast iron or ductile iron suitable for water service, or equivalent material with documented mechanical and corrosion resistance Impeller:Must be made of Ductile Iron EN-GJS-400-15 (EN 1563) or Stainless Steel EN 1.4301 (ISO 15510), or equivalent, strictly suitable for the pumped water properties. The impeller must be dynamically balanced in accordance with ISO 21940-11 (balance quality grade G2.5 or better. Shaft: High-strength stainless steel EN 1.4021 or EN 1.4401 (ISO 15510), or equivalent, corrosion-resistant Mechanical seal : The pump must be equipped with a balanced mechanical seal in accordance with EN 12756, featuring SiC/Carbon (or SiC/SiC) faces, EPDM elastomers, and AISI 316 stainless steel metal parts, or equivalent Bearings: Heavy-duty rolling bearings suitable for continuous 24/7 operation. The minimum calculated bearing operating life (L10h) must be at least 25,000 hours under maximum dynamic loads in accordance with ISO 281. Coupling: Torsionally flexible coupling with a spacer element (Spacer Coupling) to allow the "Back Pull-Out" maintenance method without dismantling the motor or piping, or equivalent. Equipped with a robust coupling guard according to EN ISO 13857. Pump Control Panel with Integrated VFD Enclosure: Powder-coated steel ≥1.5 mm, RAL 7035, IP54, IK10, indoor, floor-standing or wall-mounted, lockable door, bottom cable entry. Thermostat-controlled ventilation with replaceable filters, anti-condensation heater. Ambient −5…+40 °C, humidity ≤95% non-condensing, altitude ≤1000 m. VFD: Integrated individual VFD [45-50] kW, efficiency ≥95%, design life ≥30,000 h, conformally coated PCBs (class 3C2). Sizing: VFD power and current ≥ motor rated values. Current margin ≥10–15%, overload ≥110% for 60 s, with derating for temperature, altitude and switching frequency. Heat-loss and ventilation calculation to be provided. Supply: 3 ph, 380…480 V ±10%, 50 Hz, phase asymmetry ≤3%. Output frequency 0–500 Hz. EMC / Harmonics: Built-in EMC filter C3, built-in DC choke, THDi ≤48%. Motor cable / protection: <55 kW: shielded ≥150 m, unshielded ≥300 m without external filters. ≥55 kW: output dU/dt filter in the panel OR motor with isolated bearing. Power section & safety: Main isolator interlocked with the door, input MCCB/fuses, Type 2 SPD, supply monitoring relay (phase loss, sequence, under/overvoltage), door E-stop to STO (SIL2 / PL d), PE busbar, 360° shield clamps, ≥20% spare terminals, marked wires and terminals. Control: Vector control with auto-tuning, PID, sleep mode, pump preset Door-mounted graphical display, Local–Off–Remote selector, start/stop Fault log with time stamp RS485 Modbus RTU, USB Cascade control (pump alternation) Adjustable min/max frequency, skip frequencies, ramps Auto restart after power loss, auto fault reset kWh meter, running-hours counter Password protection, parameter backup I/O: DI/DO ≥3/2; AI/AO ≥2/1 (4–20 mA input for pressure/level); relay outputs ≥2 (Run/Fault, potential-free); motor PTC input; flood sensor input. Protections: Motor phase loss, short circuit, ground fault, motor and VFD overtemperature, over/undercurrent, over/undervoltage, dry running, pump-room flooding (alarm and trip)." | 5 |  | 20000 | Frequency converter 90 -110 kW | 6100

## Dropdown menu (hidden)
Type of Equipment |  | please choose
Notebook |  | Yes
PC |  | No
Accesorities | (Mouse, Keyboard, Docking Station..)
Office technic | Telephone,MFD, printer
Network components | Router, switch, UPS
Cartridge |  | Justification for non-neutral specification
Licence, Software |  | please choose
Monitor |  | Special manufacturing
TV |  | Compatibility/Standartization in the Project/ Partner organisation
Spare parts/ Aditional equipment/ accessories only by one Supplier
Maintenance
Category of good:
please choose
S01 Food, beverages, tobacco products
S02 Computer system
S03 Telecommunications device
S04 Standard Software rent (goods)
S05 Standard Software buy (goods)
S06 Plant Equipment, tool
S07 Construction technology
S08 Office product, facility and technic, papeterie
S09 Literature
S10 Hardware rent
S11 Energy, extraction product, secondary raw material, residue
S12 Electric engineering, automation, process control engineering
S13 Vehicle (complete vehicle)
S14 Home economics, Home technology
S15 Laboratory material, laboratory technology
S16 Installation (complete)
S17 Medical device
S18 Machine, apparatus
S19 Occupational safety, accident prevention
S20 Marketing
S21 Automotive engineering, vehicle component
S22 Human and veterinary drug, pesticide, active ingredient
S23 Clothing and textiles
S24 Body care, personal hygiene
S25 Sport, playing, leisure
S26 Interior furnishing (excl. Office furnishings)