## Specification Set 500 Wh
Position | Item | Technical Requirements for each set A comprehensive technical quotation in PDF format, including all technical data sheets, must be submitted as ONE SINGLE PDF file. | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in column A-C, please indicate "Yes". Otherwise, describe your special features in this column. Conformity of individual components with the technical specifications listed below must be proven with technical data sheets in PDF format.
1 | General Requirements
1.1 | Small-scale domestic solar power station with accessories | Small-scale domestic solar power station with accessories = Domestic basic off-grid power supply = one set The aim is to set up a small solar-powered energy system to provide basic electrification for rural households without access to other electricity supplies. The set should enable end-users to charge mobile phones and light bulbs / lamps, as well as to power small electrical appliances up to a voltage of 230V and a power rating of up to 500W. The system must be configured in such a way that it can be operated safely without any prior technical knowledge, operating on a ‘plug and play’ principle. Connectors must be designed in such a way that incorrect connection of system components is almost impossible.
1.1.1 | Capacities of solarpower station | Battery capacity min. 0,5 kWh, AC-Output 220-240 V and 500 W, DC solar input 10-50 V and min. 200 W, multisocket (Schuko, USB A and USB C).
1.2 | Power grid | The powerstation must allow the supply of electrical loads at a voltage of 230 VAC (1W+1N+1PE; 1 phase, 1 neutral conductor, 1 earth conductor)
1.3 | Basic design principles | All components must be designed to form a stand-alone system providing a simple, solar-powered basic electricity supply for a rural household with no access to any other source of electricity.. All components and parts not explicitly mentioned in this document, but necessary to ensure a sustainable and flawless operation, must be provided by the bidder (except for parts explicitly excluded from the tender).
1.4 | Components of one set | 1 x Powerstation 2 x Solarpanels incl. mounting frame 1 x cable kit to connect solarpanels to powerstation 1 x Schuko (230V) extension cable 1 x Schuko (230V) multi-socket power strip 1 x illustrated user manual 3 x rechargable and portable LED lights 3 x 3-in-1 USB charging cable
1.5 | Standards and norms | All components of the system must comply with the relevant European norms and standards.
2 | Photovolatic Modules and mounting frame
2.1 | Power of the solar panels | 100-120 W per PV-module, 2 modules
2.2 | Technical data of the module | PV modules with crystalline technology. Output per module 100-120W, tolerance 0 - 5%. Conversion rate of 23% Framed with aluminium profile (anodised). IP 68 protected Each panel including tilt mount bracket with elevation angle min 0° to 60° (stand-alone bracket)
2.3 | Product Certification | The module complies with the following certifications: CE marking of the solar modules is available. The solar modules are marked accordingly. Weatherproof junction box on the back of the module. The junction box must comply with at least IP 68 and the DIN VDE 0126-5 standard.
2.4 | Delivery | 2 PV-modules must be packed together, see point 12.2.
2.5 | Power and Product Guarantee | ≤1% Degradation in the first year, ≤0.4% Annual degradation over 30 years Product guarantee for at least 5 years
2.6 | Please specify: | Brand name, model, type
Area of the cells (LxW) in mm
Dimensions of the module (LxWxD) in mm
Weight of module in kg
Maximum power (Pmax) W
Maximum voltage ( Vmax) V
Maximum current ( Ipmax) A
Maximum reverse current IR [A]
Short-circuit current (Isc) A
Open circuit voltage ( Voc) V
Temperature coefficient for current A/°C
Temperature coefficient for voltage V/°C
Temperature coefficient for power %/°C
Nominal cell operating temperature ( NOCT)
Maximum system voltage ( Vsmax )
Operating temperature ( Min- Max ) °C
Ambient temperature ( Min - Max ) °C
Current-voltage characteristics at 25°C and other temperatures and irradiation
2.7 | Please enclose with quotation: | Data sheet
3 | Structure
3.1 | Structure | Beside tilt mount bracket for each PV-modul no further structure required.
4 | Powerstation / Inverter / battery
4.1 | Technical data of powerstation | Battery capacity min. 500Wh, min. 80% capacity aftre 3000 cycles, LFP battery Operating temperature 0°C-45°C AC-Output min. 500W (peak 1000W), Pure sine wave voltage USB-C Output min. 50W and USB-A min. 10W Solar Charging Input min. 10-50 V, min 200W Weight: max. 6,5kg LCD-Display for main operating information
4.2 | Connections / sockets | 2x 230 V AC Sockets (schuko) min. 2 USB-A outputs min. 1 USB-C output min. 1 charging input connection for solar (XT60) 1 AC charging port Bluetooth connection
4.3 | Standards | EN IEC 62368-1:2020+A11:2020 EN 62233:2008 EN 300328 V2.2.2 EN 301489-1 V2.2.3, EN 301489-17 V3.2.4 EN 55032:2015+A11:2020, EN 55035:2017+A11:2020 EN IEC 61000-3-2:2019, EN 61000-3-3:2013+A1:2019 EN IEC 62311:2020 EN IEC 63000: 2018 IEC 62321
5 | SmartSolar Charge Controller
5.1 | SmartSolar Charge Controller | not required
6 | Monitoring system
6.1 | Monitoring system | Via Android app and bluetooth connection
6.2 | Quantity of Monitoring system | 1
7 | Battery
7.1 | Lithium-ion battery | see 4.1
7.2 | Battery unit quantity | fully integrated in powerstation
8 | Cable
8.1 | Solar cables | Complete solar cable kit for connecting the two solar modules to the power station; minimum cable length between the PV modules and the power station = 10 m high flame resistance and high UV resistance. The standard EN 50618 is fulfilled. Please calculate required diameters according to cable lengths and for a fully functional system operation. Solar DC wiring must be carried out in accordance with IEC 62930:2017.
9 | Accessories / Others
9.1 | LED lights | 3 x Rechargeable LED Lamps; charging port USB-C or Micro-USB; Luminance: 1 x 150 lumen, 1 x 250lumen, 500-600lumen; Cool white or adjustable light colour, glare-free light source; Hemispherical light distribution; Each lamp must be used as a table lamp or a hanging lamp (wtih a hook)
9.2 | Extension cable and multi-socket power strip | 1 x Schuko (230V) extension cable, wire diametre min. 1,5mm2, 20m length, IP44 protected 1 x Schuko (230V) multi-socket power strip, min. 3 sockets, power switch, wire diametre min. 1,5mm2, 3m length, IP44 protected
9.3 | 3-in-1 USB charging cable | USB-Charging cable with USB-A, USB-C and USB-Micro socket length min. 0,5m 3 x cables per set required
10 | Documentation
10.1 | The following documentation must be supplied in electronic form for the set after the order has been placed: | An illustrated user guide, suitable for illiterate users, covering initial commissioning, operation and cleaning (as PDF-File)
10.2 |  | A compilation of the operating instructions and technical specifications for all individual components in French (as PDF-File)
11 | Spare parts (per set)
11.1 | Spare parts | not required
12 | Material Delivery
12.1 | Delivery | All material must be delivered DPU GIZ Country Office Niamey in Niger latest four months after order.
12.2 | Packaging | Each set must be packed individually, divided into a maximum of two packages (e.g. package 1 = solar panels, package 2 = power station, lamps, cables, module mounts, small parts)
12.3 | Please specify: | Dimensions of packaging for sea and truck shipment.
12a | Customs clearance (by giz)
| Customs clearance (by giz) | Customs clearance will be done by giz.
13 | Warranty
13.1 | min. 2 years | On the entire system. Fully according to GIZ General Purchase Conditions (GPC) 2023. The claims arising from the product and system warranties apply in addition to the claims for defects in accordance with GIZ GPC 2023.
13.2 | Place of validity | All guarantee and warranty conditions apply at the location of delivery. Even if the material was handed over at other locations. This applies only insofar as the locations of the installed systems are accessible. Otherwise, spare parts must be delivered to the nearest GIZ office and technical support must be provided remotely.
13.3 | Guarantee assignment declarations | All warranties must be assigned to GIZ and project partners by declaration. This declaration must be signed and stamped by each manufacturer.

## Specification Set 10 kWh
Position | Item | Technical Requirements for each set A comprehensive technical quotation in PDF format, including all technical data sheets, must be submitted as ONE SINGLE PDF file. | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in column A-C, please indicate "Yes". Otherwise, describe your special features in this column. Conformity of individual components with the technical specifications listed below must be proven with technical data sheets in PDF format.
1 | General Requirements
1.1 | Mini off-grid solar system for agricultural producers | Mini off-grid solar system for agricultural producers = one set The aim is to set up a mini off-grid solar energy system to provide electrification in rural areas for agricultural producers without access to other electricity supplies. The kit is designed to enable agricultural producers to operate basic electrical equipment autonomously in single-phase mode for transforming and/or conserving of agricultural products, up to a voltage of 230V and a power rating of up to 3600W. The system must be configured in such a way that it can be operated safely without any prior technical knowledge, operating on a ‘plug and play’ principle. Connectors must be designed in such a way that incorrect connection of system components is almost impossible.
1.1.1 | Capacities of solarpower station | Battery capacity min. 10 kWh, AC-Output 220-240 V and max. 3600 W, DC solar input 16-50 V and ca. 8 kWp
1.2 | Power grid | The powerstation must allow the supply of electrical loads at a voltage of 230 VAC (1W+1N+1PE; 1 phase, 1 neutral conductor, 1 earth conductor) = single phase
1.3 | Basic design principles | All components must be designed to form a stand-alone off-grid system providing a simple, solar-powered electricity supply for a rural agricultural producers with no access to any other source of electricity.. All components and parts not explicitly mentioned in this document, but necessary to ensure a sustainable and flawless operation, must be provided by the bidder (except for parts explicitly excluded from the tender).
1.4 | Components of one set | 1 x Headunit (inverter + battery) 1 x additionnal battery 8 x Solarpanels incl. mounting structure 1 x cable kit to connect solarpanels to powerstation 1 x Schuko (230V) extension cable 1 x Schuko (230V) multi-socket power strip 1 x illustrated user manual
1.5 | Standards and norms | All components of the system must comply with the relevant European norms and standards.
2 | Photovolatic Modules and mounting frame
2.1 | Power of the solar field | 3,7 to 4 kWp, 8 PV modules per set.
2.2 | Technical data of the module | PV modules with crystalline technology. Output per module 465-500 W, tolerance 0 - 5%. Certification for wind load in Sahel region. Solar cells are embedded in an EVA (ethylene vinyl acetate) layer, anti-reflective coating, front cover made of specially tempered, highly transparent glass. Framed with aluminium profile (anodised).
2.3 | Product Certification | The module complies with the following certifications: - IEC 61 215 : Terrestrial photovoltaic (PV) modules - Type qualification and type approval. - IEC 61 730 : Photovoltaic (PV) modules - safety qualification The tests are carried out by recognised testing laboratories according to ISO/IEC 17025. The manufacturer of the solar modules can prove by a suitable certificate that a permanent quality control and assurance of the production processes takes place in his factory. It must be proven that the standards according to IEC 61215 and IEC 61730 are also adhered to in ongoing production. The certificate itself is issued by an accredited testing institute. The normative requirements IEC 60891 ; IEC 60904 ; IEC 61345 ; IEC 61701; IEC 61721; EN 50380 are fulfilled. CE Declaration of Conformity by the manufacturer is available. A confirmation by a conformity assessment body according to ISO/IEC 17021 is available. CE marking of the solar modules is available. The solar modules are marked accordingly. Weatherproof junction box on the back of the module. The junction box must comply with at least IP 65 and the DIN VDE 0126-5 standard. The cabling between the modules with connectors complies with the EN 50521 standard.
2.4 | Power and Product Guarantee | ≤1% Degradation in the first year, ≤0.4% Annual degradation over 30 years Product guarantee for at least 5 years
2.5 | Please specify: | Brand name, model, type
Area of the cells (LxW) in mm
Dimensions of the module (LxWxD) in mm
Weight of module in kg
Maximum power (Pmax) W
Maximum voltage ( Vmax) V
Maximum current ( Ipmax) A
Maximum reverse current IR [A]
Short-circuit current (Isc) A
Open circuit voltage ( Voc) V
Temperature coefficient for current A/°C
Temperature coefficient for voltage V/°C
Temperature coefficient for power %/°C
Nominal cell operating temperature ( NOCT)
Maximum system voltage ( Vsmax )
Operating temperature ( Min- Max ) °C
Ambient temperature ( Min - Max ) °C
Current-voltage characteristics at 25°C and other temperatures and irradiation
2.6 | Please enclose with quotation: | Data sheet
3 | Structure
3.1 | Structure | The substructure made of aluminium or stainless steel must support the modules. It must be sufficiently protected against corrosion; Inclination angle of the PV 15 - 20° relative to the horizontal plane; Mounting on the ground, in two rows of four modules each; Special anti-theft bolts and nuts to match the modules; Lightning protection and earthing
3.2 | Ground conditions | From laterite soil to sandy subsoil
3.3 | Manufacturer Warranty | min. 10 years
3.4 | Please specify: | Brand name, model, type
Data sheet
Detailed description of the anti-theft screws and nuts
Technical description of the substructure
Description of the lightning protection
3.5 | In case of order, to be provided before delivery: | Sectional drawings of the profiles and elevations
Detailed drawings of fixings (interfaces, connections)
Assembly instructions in French
4 | Head unit / Inverter / battery
4.1 | Total inverter capacity | 5 kVA, 4 MPPT (strings)
4.4 | System output voltage and power | 220 / 230 VAC, 50Hz (L+N+PE) Off-Grid AC-Power Output min. 2500W and peak up to 3600W
4.5 | Unit capacity of inverters | 5 kVA
4.6 | Inverter unit | The following functions are fulfilled: - enables supply of consumers with 220 V AC - charges the battery with an integrated MPPT charge controller - U-I generator diagnosis - Protective conductor monitoring - Max. apparent feed-in power: 5 000 VA
4.7 | Capacity unit and technical data | Continuous input power 5 000 VA (4 x 1250 VA) max. input voltage 60 VDC Integrated MPP tracker, 4 MPPT, multi-stage charging technology Output voltage 220 V AC +/- 5%, schuko sockets Output frequency 50/60 Hz Pure sine wave voltage Battery capacity inside head unit min. 5kWh, min. 80% capacity aftre 8000 cycles, LFP battery Operating temperature up to 55°C Weight head unit: max. 55kg LCD-Display for main operating information IP 66 protectet; Bluetooth connection; Directly stackeble on top of additional battery modules
4.8 | Standards | EN IEC 62311: 2020 EN 50665:2017, EN 55032:2015+A1:2020, EN 55032:2015+A11:2020, EN 55035:2017+A11:2020 EN IEC 61000-6-1:2019, EN IEC 61000-6-3:2021, EN IEC 61000-3-2:2019+A1:2021, EN 61000-3-3:2013/A2:2021
4.9 | Quantity of head units | 1 per set
5 | SmartSolar Charge Controller
5.1 | SmartSolar Charge Controller | not required
6 | Monitoring system
6.1 | Monitoring system | Via Android app and bluetooth connection
6.2 | Quantity of Monitoring system | 1
7 | Battery
7.1 | Lithium-ion battery | Nominal voltage 16V DC, max. charge and discharge current 180 A DC; 5kWh, 314 Ah; Weight battery pack: max. 45kg IP 66 protectet; stackable under head unit;
7.2 | Battery unit quantity | 1 additional modul per set (Total battery capacity head unit + add. Battery modul = 10kWh)
8 | Cable
8.1 | Solar cables | Complete solar cable kit for connecting the solar modules to the head unit; minimum cable length between the PV modules and head unit = 20 m high flame resistance and high UV resistance. The standard EN 50618 is fulfilled. Please calculate required diameters according to cable lengths and for a fully functional system operation. Solar DC wiring must be carried out in accordance with IEC 62930:2017.
9 | Accessories / Others
9.1 | Extension cable and multi-socket power strip | 1 x Schuko (230V) extension cable, wire diametre min. 1,5mm2, 20m length, IP44 protected 1 x Schuko (230V) multi-socket power strip, min. 3 sockets, power switch, wire diametre min. 1,5mm2, 3m length, IP44 protected
10 | Documentation
10.1 | The following documentation must be supplied in electronic form for the set after the order has been placed: | An illustrated user guide, suitable for illiterate users, covering initial commissioning, operation and cleaning (as PDF-File)
10.2 |  | A compilation of the operating instructions and technical specifications for all individual components in French (as PDF-File)
11 | Spare parts (per set)
11.1 | Spare parts | not required
12 | Material Delivery
12.1 | Delivery | All material must be delivered DPU GIZ Country Office Niamey in Niger latest four months after order.
12.2 | Packaging and labeling | Each set must be packed and labelled in such a way that the various packing containers can be dispatched unambiguously and without any risk of mix-ups
12.3 | Please specify: | Dimensions of packaging for sea and truck shipment.
12a | Customs clearance (by giz)
| Customs clearance (by giz) | Customs clearance will be done by giz.
13 | Warranty
13.1 | min. 2 years | On the entire system. Fully according to GIZ General Purchase Conditions (GPC) 2023. The claims arising from the product and system warranties apply in addition to the claims for defects in accordance with GIZ GPC 2023.
13.2 | Place of validity | All guarantee and warranty conditions apply at the location of delivery. Even if the material was handed over at other locations. This applies only insofar as the locations of the installed systems are accessible. Otherwise, spare parts must be delivered to the nearest GIZ office and technical support must be provided remotely.
13.3 | Guarantee assignment declarations | All warranties must be assigned to GIZ and project partners by declaration. This declaration must be signed and stamped by each manufacturer.