## Specification
Lot | Position | Item description | Minimum Requirements | Quantity [pcs.] | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns B-E, please indicate "Yes". Otherwise, describe your special features in this column.
all lots |  | General requirement | Availability of an authorized service center in Ukraine. In the event of a warranty case, the center must resolve the issue within 60 days from the date of application.
1 | 1.1 | Monobloc pump, Q=10-12m³/h, H=30-40m | Glandless pump with flange connection Installation: internal Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: water of heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN 16 Characteristics of pump perfomance at the operating point: Capacity: 10-12 m³/h Head: 30-40 m Hydraulic efficiency: not less than 50% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
| 1.2 | Monobloc pump, Q=10-12m³/h, H=25-35m | Glandless pump with flange connection Installation: internal Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: water from heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN16 Characteristics of pump perfomance at the operating point: Capacity: 10-12 m³/h Head: 25-35 m Hydraulic efficiency: not less than 50% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
| 1.3 | Monobloc pump, Q=250-275 m³/h, H=60-70m | Glandless pump with flange connection Installation: internal Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids water from heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN16 Characteristics of pump perfomance at the operating point: Capacity: 250-275 m³/h Head: 60-70 m Hydraulic efficiency: not less than 75% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
| 1.4 | Monobloc pump, Q=350-375m³/h, H=70-80m | Glandless pump with flange connection Installation: internal Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped media: water of heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN16 Characteristics of pump perfomance at the operating point: Capacity: 350-375 m³/h Head: 70-80 m Hydraulic efficiency: not less than 75% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 5
2 | 2.1 | In-line circulation pump Q=200-225m³/h, H=34-40m | Single inline pump with dry rotor and flange connection Installation: internal version Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped media: water from heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN16 Characteristics of pump perfomance at the operating point: Capacity: 200-225 m³/h Head: 34-40 m Hydraulic efficiency: not less than 75% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
| 2.2 | In-line circulation pump Q=39-45m³/h, H=31-40m | Single inline pump with dry rotor and flange connection Installation: internal version Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: water from heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN 16 Characteristics of pump perfomance at the operating point: Capacity: 39-45 m³/h Head: 31-40 m Hydraulic efficiency: not less than 65% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
| 2.3 | In-line circulation pump Q=34-40m3/h, H=9-15m | Single inline pump with dry rotor and flange connection Installation: internal version Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: water from heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN16 Characteristics of pump perfomance at the operating point: Capacity: 34-40 m³/h Head: 9-15 m Hydraulic efficiency: not less than 60% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
| 2.4 | In-line circulation pump Q=14-20m3/h, H=51-60m | Single inline pump with dry rotor and flange connection Installation: internal version Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped media: water of heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN16 Characteristics of pump perfomance at the operating point: Capacity: 14-20 m³/h Head: 51-60 m Hydraulic efficiency: not less than 50% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
| 2.5 | In-line circulation pump Q=18-25m3/h, H=49-55m | Single inline pump with dry rotor and flange connection Installation: internal version Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: water from heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN16 Characteristics of pump perfomance at the operating point: Capacity: 18-25 m³/h Head: 49-55 m Hydraulic efficiency: not less than 50% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
| 2.6 | In-line circulation pump Q=69-75m³/h, H=25-35m | Single inline pump with dry rotor and flange connection Installation: internal version Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: water from heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN 16 Characteristics of pump perfomance at the operating point: Capacity: 69-75 m³/h Head: 25-35 m Hydraulic efficiency: not less than 70% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
| 2.7 | In-line circulation pump Q=300-325m³/h, H=50-60m | Single inline pump with dry rotor and flange connection Installation: internal version Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: water from heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN 16 Characteristics of pump perfomance at the operating point: Capacity: 300-325 m³/h Head: 50-60 m Hydraulic efficiency: not less than 65% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 2
3 | 3.1 | Cantilever circulation pump Q=325-350m³/h, H=94-105m | Single-stage low-pressure centrifugal pump with axial suction on a common frame. Standard version with collapsible coupling. Installation: internal version Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: water from heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN 16 Characteristics of pump perfomance at the operating point: Capacity: 325-350 m³/h Head: 94-105 m Hydraulic efficiency: not less than 80% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
| 3.2 | Cantilever circulation pump Q=240-270m³/h, H=70-80m | Single-stage low-pressure centrifugal pump with axial suction on a common frame. Standard version with collapsible coupling. Installation: internal version Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped media: water from heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +120°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN 16 Characteristics of pump perfomance at the operating point: Capacity: 240-270 m³/h Head: 70-80 m Hydraulic efficiency: not less than 75% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 2
| 3.3 | Cantilever circulation pump Q=700-750m³/h, H=75-90m | Pump with axial-split casing on a common frame Installation: internal Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: water of heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +100°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN16 Pump performance characteristics at the operating point: Capacity: 700-750 m³/h Head: 75-90 m Hydraulic efficiency: not less than 75% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
4 | 4.1 | Double-entry circulation pump Q=200-225m³/h, H=90-100m | Pump with axial-split casing, with working medium inlet from both sides, on a common frame Installation: internal Characteristics of engine: Number of network phases: 3 Rated network voltage: 380...480 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: water of heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +100°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN16 Pump performance characteristics at the operating point: Capacity: 200-225 m³/h Head: 90-100 m Hydraulic efficiency: not less than 70% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
5 | 5.1 | Multistage pump Q=25-30m³/h, H=210-230m | Normal suction multistage centrifugal high-pressure pump in vertical design with inline connection Installation: internal Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: water of heating systems according to VDI 2035 or equivalent Maximum pumped liquids temperature: not less than +90°C Permissible operating pressure: not less than 25 bar Pump connection: flanged Permissible flange pressure: not less than PN 25 Pump performance characteristics at the operating point: Capacity: 25-30 m³/h Head: 210-230 m Hydraulic efficiency: not less than 65% Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 2
6 | 6.1 | Deep well pump Q=352-362m3/h, H=121-131m | Housing - cast stainless steel with a submersible motor in a sectional design Installation: vertical and horizontal mounting, external design, submersible Characteristics of engine: Number of network phases: 3 Rated network voltage: 1000 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP68 Electric motor power - 165-200 kW Characteristics of pumped liquids: Permissible pumped liquids: drinking, spring, well water Maximum pumped liquids temperature: not less than +25°C Permissible operating pressure: not less than 25 bar Pump connection: flange Permissible flange pressure: not less than PN 25 Pump performance characteristics at the operating point: Capacity: 352 - 362 m³/h Head: 121 - 131 m Hydraulic efficiency: not less than 75% Pump equiped with temperature sensor PT100 type and power cable 130 m Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
7 | 7.1 | Sewage pump Q= 200-210 m³/h, H=30-40m | Sewage pump Installation: internal Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: sewage with feces Maximum pumped liquids temperature: not less than +40°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN 16 Pump performance characteristics at the operating point: Capacity: 200-210 m³/h Head: 30-40 m Hydraulic efficiency: not less than 55%. Accomplish to seria of standarts EN 12050 / directive 60335-2-41 or equivalent Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1
| 7.2 | Sewage pump Q=250-270 m³/h, H=20-30m | Sewage pump Installation: internal Characteristics of engine: Number of network phases: 3 Rated network voltage: 400 V +/-10% Rated network frequency: 50 Hz +4/-6% Energy efficiency class: not less than IE3 Insulation class: not less than F Protection class: not less than IP55 Characteristics of pumped liquids: Permissible pumped liquids: sewage with feces Maximum pumped liquids temperature: not less than +40°C Permissible operating pressure: not less than 16 bar Pump connection: flange Permissible flange pressure: not less than PN 16 Pump performance characteristics at the operating point: Capacity: 250-270 m³/h Head: 20-30 m Hydraulic efficiency: not less than 55% Accomplish to seria of standarts EN 12050 / directive 60335-2-41 or equivalent Compliance with IEC 60034-1, DIN EN 809 or equivalent. | 1

## Delivery Plan
No. | Delivery address | Position (quantity for delivery, pcs)
| The delivery schedule contains only the location details. A detailed address will be provided for each location after order. | 1.1 | 1.2 | 1.3 | 1.4 | 2.1 | 2.2 | 2.3 | 2.4 | 2.5 | 2.6 | 2.7 | 3.1 | 3.2 | 3.3 | 4.1 | 5.1 | 6.1 | 7.1 | 7.2
1 | Cherkasy city, Cherkasy region | 1 | 1 | 1
2 | Smila town, Cherkasy region |  |  |  |  | 1 | 1 | 1 | 1 | 1
3 | Monastyryshche town, Cherkasy region | [9 empty] | 1
4 | Teplodar town, Odesa region | [15 empty] | 2
5 | Vyshgorod city, Kyiv region | [11 empty] | 1
6 | Mykolaiv city, Mykolaiv region | [13 empty] | 1
7 | Pryluky city, Chernihiv region | [14 empty] | 1
8 | Chernihiv city, Chernihiv region | [16 empty] | 1
9 | Lviv city, Lviv region | [12 empty] | 2
10 | Kropyvnytskyi, Kirovograd region |  |  |  | 5
11 | Novovolynsk, Volynskiy region | [10 empty] | 2
12 | Svitlovodsk, Kirovograd region | [17 empty] | 1 | 1
|  | 1 | 1 | 1 | 5 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1

## Overview
Lot | Position | Item description | Water | Quantity [pcs.]
1 | 1.1 | Monobloc pump, Q=10-12m³/h, H=30-40m | hot water | 1
| 1.2 | Monobloc pump, Q=10-12m³/h, H=25-35m |  | 1
| 1.3 | Monobloc pump, Q=250-275 m³/h, H=60-70m |  | 1
| 1.4 | Monobloc pump, Q=350-375m³/h, H=70-80m |  | 5
2 | 2.1 | In-line circulation pump Q=200-225m³/h, H=34-40m |  | 1
| 2.2 | In-line circulation pump Q=39-45m³/h, H=31-40m |  | 1
| 2.3 | In-line circulation pump Q=34-40m3/h, H=9-15m |  | 1
| 2.4 | In-line circulation pump Q=14-20m3/h, H=51-60m |  | 1
| 2.5 | In-line circulation pump Q=18-25m3/h, H=49-55m |  | 1
| 2.6 | In-line circulation pump Q=69-75m³/h, H=25-35m |  | 1
| 2.7 | In-line circulation pump Q=300-325m³/h, H=50-60m |  | 2
3 | 3.1 | Cantilever circulation pump Q=325-350m³/h, H=94-105m |  | 1
| 3.2 | Cantilever circulation pump Q=240-270m³/h, H=70-80m |  | 2
| 3.3 | Cantilever circulation pump, Q=700-750m³/h, H=75-90m |  | 1
4 | 4.1 | Double-entry circulation pump Q=200-225m³/h, H=90-100m |  | 1
5 | 5.1 | Multistage pump Q=25-30m³/h, H=210-230m |  | 2
6 | 6.1 | Deep well pump Q=352-362m3/h, H=121-131m | cold water | 1
7 | 7.1 | Sewage pump, Q= 200-210 m³/h, H=30-40m | wastewater canalization | 1
| 7.2 | Sewage pump, Q=250-270 m³/h, H=20-30m |  | 1

## Dropdown menu (hidden)
Type of Equipment |  | please choose
Notebook |  | Yes
PC |  | No
Accesorities | (Mouse, Keyboard, Docking Station..)
Office technic | Telephone,MFD, printer
Network components | Router, switch, UPS
Cartridge |  | Justification for non-neutral specification
Licence, Software |  | please choose
Monitor |  | Special manufacturing
TV |  | Compatibility/Standartization in the Project/ Partner organisation
Spare parts/ Aditional equipment/ accessories only by one Supplier
Maintenance
Category of good:
please choose
S01 Food, beverages, tobacco products
S02 Computer system
S03 Telecommunications device
S04 Standard Software rent (goods)
S05 Standard Software buy (goods)
S06 Plant Equipment, tool
S07 Construction technology
S08 Office product, facility and technic, papeterie
S09 Literature
S10 Hardware rent
S11 Energy, extraction product, secondary raw material, residue
S12 Electric engineering, automation, process control engineering
S13 Vehicle (complete vehicle)
S14 Home economics, Home technology
S15 Laboratory material, laboratory technology
S16 Installation (complete)
S17 Medical device
S18 Machine, apparatus
S19 Occupational safety, accident prevention
S20 Marketing
S21 Automotive engineering, vehicle component
S22 Human and veterinary drug, pesticide, active ingredient
S23 Clothing and textiles
S24 Body care, personal hygiene
S25 Sport, playing, leisure
S26 Interior furnishing (excl. Office furnishings)