## Specification
Position | Item | Description | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns A-C, please indicate "Yes". Otherwise, describe your special features in this column.
1 | General Requirements
1.1 | PV Plant | Total system size 2,500 kWp + 5% spare part modules The project comprises 100 PV systems across 5 states. Please find attached the breakdown of site-specific capacities for all 100 sites. State breakdown: Akwa Ibom - 20 sites; Plateau - 20 sites; Enugu - 29 sites; Abia - 14 sites(PH_01 and 02 forms part of spare); Ogun - 17 sites All minimum requirements are defined in tab "Site-Specific Capacities"! - Ground-mounted system/ - Battery storage/ - Hybrid connection available
1.2 | Site conditions | The plants are to be erected in Nigeria across five states (Akwa Ibom, Plateau, Enugu, Abia, Ogun). Ambient temperatures range from 5°C to 40°C; relative humidity up to 100% RH (southern sites: salt mist environment per IEC 60721-3 class 4C2). Maximum structural design wind speed: 160 km/h (44 m/s) at 10 m height, 50-year return period. Installation height: 40–1,300 m above sea level. Dust/sand exposure per IEC 60721-3 class 4S2. All components must be designed, rated, and type-tested accordingly.
1.3 | Power grid | Systems shall be designed for off-grid operation as the primary mode. Where a grid connection is available at a given site, the system shall be capable of grid-tied or hybrid operation; grid operator technical requirements shall apply at those sites only.
1.4 | Basic design principles | The components offered must be fully functional and compatible with each other and operationalise the system without further requirement/addition All components and parts that are not explicitly mentioned in this document, but are necessary to ensure a faultless room layout, installation and professional operation must be offered by the bidder (except for parts that are explicitly excluded from the tender).
1.5 | Standards and norms | The standards mentioned here may also be offered by equivalent standards as long as they cover the same requirements.
2 | Photovolatic Modules
2.1 | Photovolatic Modules | 144 half-cut cell (72 full-cell equivalent) PV modules with crystalline silicon technology, N-type TOPCon or HJT (Bifacial). Output per module: minimum 550 Wp, maximum 600 Wp; power tolerance: 0 to +5% (no negative tolerance). Bifacial gain: indicative 5–10% subject to site-specific albedo and installation geometry; bidder to declare assumed bifacial gain per site category in yield calculations. Mechanical load certification: ≥2,400 Pa front load and ≥2,400 Pa rear load per IEC 61215 mechanical load test. Snow load certification not applicable (Nigeria). Structural mounting system to be independently verified for 160 km/h (44 m/s) design wind speed. Encapsulant: POE (Polyolefin Elastomer); front cover: 3.2 mm AR-coated, anti-reflective, tempered high-transmission glass. Frame: aluminium profile, marine-grade anodised (≥40 mm profile depth, anodising layer ≥15 µm per ISO 7599); anti-corrosion rated. NOCT: ≤46°C (to be declared by manufacturer and used in yield modelling). Module efficiency: ≥22.5%. Temperature coefficient of Pmax: ≤ -0.30%/°C (i.e., not more negative than -0.30%/°C; applies uniformly throughout this specification). PID-free (inherent for N-type TOPCon and HJT); anti-LID. Anti-dust / self-cleaning coating: optional but preferred. Connectors: genuine MC4 (Stäubli) or MC4-compatible type, certified to IEC 62852, IP68-rated, with UV-resistant housing rated for ≥25 years outdoor exposure. Counterfeit or uncertified connectors are not acceptable. Factory pre-assembled cable leads: minimum 1,200 mm per polarity (positive and negative), compliant with IEC 62930 (PV wire), 6 mm² Cu conductor, double-insulated, UV-resistant. No field-assembled connectors required for module-to-module connections. Documentation: English language only. All PV modules must be from manufacturers classified as Tier 1 by BloombergNEF's latest published quarterly ranking at time of tender. Tier 1 classification is a minimum eligibility criterion; modules must additionally carry valid IEC 61215 and IEC 61730 certifications from an accredited test laboratory (see Section 2.2).
2.2 | Certifications and standards | The module complies with the following certifications: - IEC 61 215 : Terrestrial photovoltaic (PV) modules - Type qualification and type approval. - IEC 61 730 : Photovoltaic (PV) modules - safety qualification - IEC 62782 tested The tests are carried out by recognised testing laboratories according to ISO/IEC 17025. The manufacturer of the solar modules can prove by a suitable certificate that a permanent quality control and assurance of the production processes takes place in his factory. It must be proven that the standards according to IEC 61215 and IEC 61730 are also adhered to in ongoing production. The certificate itself is issued by an accredited testing institute. The normative requirements IEC 60891 ; IEC 60904 ; IEC 61345 ; IEC 61701; IEC 61721; EN 50380 are fulfilled. CE Declaration of Conformity by the manufacturer is available. A confirmation by a conformity assessment body according to ISO/IEC 17021 is available. CE marking of the solar modules is available. The solar modules are marked accordingly. Weatherproof junction box on the back of the module. The junction box must comply with at least IP 65 and the DIN VDE 0126-5 standard. The cabling between the modules with connectors complies with the EN 50521 standard. IEC 61215/61730, UL 61730, Salt Mist Corrosion (IEC 61701) Certification body - SGS or Intertek IEC TS 63209 (extended reliability testing) IEC 62804 (Potential Induced Degradation test) TÜV Rheinland or VDE certification required
2.3 | Delivery | The modules must be packed in wooden boxes or equivalent. IEC 62759-1 shall be observed with regard to the delivery/shipping of the modules. Flash data for each module must be provided as a digital file.
2.4 | Warranty | 15 years product warranty and Linear performance guarantee 30-year (≥87% at End of Life) with maximum degradation coefficient of ≤-0.43%/year Pmax coefficient >-0.30%/°C If the rated power of the modules is undershot within the guaranteed warranty period, the modules will be replaced free of charge at the installation site in Nigeria.
2.5 | Please specify: | Brand name, model, type
Area of the cells (LxW) in mm
Dimensions of the module (LxWxD) in mm
Weight of module in kg
Maximum power (Pmax) W
Maximum voltage ( Vmax) V
Maximum current ( Ipmax) A
Maximum reverse current IR [A]
Short-circuit current (Isc) A
Open circuit voltage ( Voc) V
Temperature coefficient for current A/°C
Temperature coefficient for voltage V/°C
Temperature coefficient for power %/°C
Nominal cell operating temperature ( NOCT)
Maximum system voltage ( Vsmax )
Operating temperature ( Min- Max ) °C
Ambient temperature ( Min - Max ) °C
Current-voltage characteristics at 25°C and other temperatures and irradiation
2.6 | Please enclose with quotation: | Data sheet
Test certificates according to IEC 61215 and IEC 61730
Certificates according to ISO/IEC 17025
Accreditation of the test centre/institute or test centres (IEC 61215, IEC 61730 and ISO/IEC 17025) according to EN 45011 - 45013
CE declaration of conformity of the manufacturer
Confirmation that upon delivery of the modules, the flasher protocols showing the rated power of all delivered modules are presented and handed over. Third-party PSI: Hire SGS/Intertek for batch sampling
Declaration or explicit confirmation regarding the replacement of the modules according to item 2.3.
Explanations on packaging and handling of the solar modules with reference to IEC 62759-1
2.7 | EL measurements | The results and images of the flash tests and electroluminescence measurements issued to the serial numbers of the panels shall be submitted. All documents and technical documentation submitted must be legible and easily recognisable. Flash Test Enforcement Inclusion of contract clauses: "100% flash test reports required before shipment. QR-linked flash reports for individual module Demand EL (electroluminescence) tests to detect microcracks. IV curve testing on-site after installation. All certfications must be present before Shipment.
3 | Structure
3.1 | Structure + 5% spare parts | The substructure made of Hot-dip galvanized steel (≥86μm) or aluminum (ZM 310 coating) must support the modules and withstand the local weather conditions. It must be sufficiently protected against corrosion. IEC 61701 salt-mist certification Angle of inclination: [10 - 15]° Foundation Screw piles Row Spacing ≥1.5x module height Corrosion Protection Stainless steel fasteners + rubberized clamps Wind Rating ≥2400Pa (with 1.5x safety factor) Special anti-theft bolts and nuts to match the modules. Lightning protection and earthing Installation Height Above Sea Level: 40–300 m Where soil conditions preclude screw pile installation (e.g., laterite hardpan or rocky subsoil, particularly relevant to Plateau State sites), concrete ballasted or surface-mounted ground frames are acceptable, subject to structural engineer sign-off and written approval by GIZ/NTU. See attached indicative preliminary foundation depths for the PV Mounting Structure.
3.3 | Warranty | min. 15 years
3.4 | Please specify: | Brand name, model, type
Data sheet
Detailed description of the anti-theft screws and nuts
Technical description of the substructure
Description of the lightning protection
3.5 | In case of order, to be provided before delivery: | Sectional drawings of the profiles and elevations
Detailed drawings of fixings (interfaces, connections)
Assembly instructions in English
4 | Inverter
| Inverter (see attached site specific capacities) 100 systems + 10% spare units (see note) Note: 100 inverter systems correspond to 100 project sites. An additional 10% spare/replacement unit allocation is required. For sites ≥100 kWp (9 sites), parallel/stacked inverter units will be required; exact unit count per site to be confirmed by system designer per final SLD. | The following functions and specifications are fulfilled: - Nominal AC power must be Minimum capacities of the attached document in 1.1 , and must be scalable. The system should be uniform across the sites and align with site specific capacities attached. (Scalable here refers to the system’s ability to grow with additional capacity and adapt to increasing energy needs over time. Therefore, the system should be able to allow for the addition of more capacity- whether in generation, or storage, without requiring a replacement. This ensures long-term sustainability and flexibility to meet future demand.) - enables supply of consumers with 230/415 V AC; 3L+PE+N - charges the battery with an integrated MPPT charge controller with PV capacity - simultaneously allows connection to a generator or power grid (0.415VAC) - U-I generator diagnosis and integrated with: - Protective conductor monitoring - Reverse DC Connection Protection - Anti-Islanding Protection - Over-Temperature Protection - Grid Monitoring/Earthing fault Detection - DC/AC Surge protection; Type II - Insulation Monitoring - Internal integration of battery racks, BMS, EMS, and control systems - Must be capable to work on off-grid and grid tied mode(Hybrid), 100% unbalanced load capacity in off-grid operation - Fully insulated IP65 modular cabinet for outdoor installation with anti-corrosion class C4 minimum. Operation Temperature Range 2 - 60℃(45℃ > Derating) - THDi <3%, ≥98% Efficiency
Parallel and 3-phase operation with active load balancing Smart load prioritization ≥96.5% inverter CEC, ≥98% MPPT efficiency Compatible with LiFePO4 batteries Grid Monitoring/Earthing fault Detection - Scalable Containerized Microgrid System IP65, Support outdoor installation for all the components (i.e; battery, inverter, BMS etc) secured in a hash environment comprising with intelligent air cooling - Intelligent Microgrid Controller Hardware + Software, Remote Energy Access Cloud Platform. - EMS Software platform and API access and Integration to a third-party platform(Prospect Platform) - HVAC Management & Protection system - LT switchgear (C&S/L&T/CHINT/EQ) and Insulation Monitoring system - Critical spares to be maintained at site
| Capacity | Output voltage 230/415 V AC +/- 5% Output frequency 50/60 Hz Pure sine wave voltage Integrated MPP tracker, multi-stage charging technology to support minimum PV capacity integrated with Power and Energy limiters, Current limiting fuses, insulation resistance and alarm system DC / AC-coupled solar-storage Adjustable end-of-charge voltages badjusted to the interconnecting solar modules from position 2 and, if applicable, known consumer devices. Input voltage 90 - 415 V AC Input frequency 45 - 65 Hz; automat. Automatic recognition 50/60 Hz (415 V, 3-phase, IP55/IK10, floor-standing equipment enclosure/cabinet) Integrated self-developed BMS / EMS for flexibility
| Handling | Graphic LCD display or or simply connect it to a standard mobile device Menu-guided operation Serial interface RS-232, PC connection via USB Incl. PC software
| Power protection | Overcharge protection Reverse polarity protection of modules, for battery via fuses Deep discharge protection Short-circuit protection of load and module Reverse polarity protection via internal fuses Reverse current protection at night Overtemperature and overload protection Audible alarm PE connection
| Certifications and standards | It must comply with the following standards: EN-IEC 62040, EN-IEC 60335-2-29, EN 55014-1, EN 55014-2, IEC 62109-1/2 (safety for PV inverters). IEC 61727 (grid connection). IEC 61683 (inverter efficiency). EN 50549 (grid code compliance). EN 55014-1/2, EN-IEC 61000-3-2, IEC 61000-6-1/2/3 (EMC). Nigerian Electricity Regulatory Commission (NERC) grid code. Quality: Manufactured in facilities certified to ISO 9001, ISO 14001, and ISO 50001. Compliance: CE marking, TÜV Rheinland or VDE certification required. Testing: Factory witness testing by SGS or Intertek for major components. Manufacturers: Inverters must be from tier 1 manufacturers per BloombergNEF’s latest quarterly ranking
| Additional Requirements | Data Sheet: Submit detailed datasheet specifying brand name, model, and type. Test Certificates: Provide IEC 62109-1/2, IEC 61727, and ISO/IEC 17025 certificates from accredited testing institutes (SGS, Intertek, TÜV Rheinland, or VDE). Spares Inventory: Include 5% extra fuses, control boards, and MC4 connectors on-site. Blockchain Tracking: QR codes on each inverter linking to test data and serial numbers. AC-Coupled Systems: Submit datasheets for energy meters and communication modules. Commissioning: Include functional tests and trial operation, with training for Nigerian certified technicians on operation and maintenance. Bidders proposing AC-coupled solutions must submit: Proof of ≥3 deployments >50kW in tropical climates (≥35°C) Heat derating curves certified by TÜV/SGS Network diagram showing component interoperability. All components offered must be recyclable, repairable, and supported by the availability of spare parts.
| Warranty | min. 10 years. Bank-backed, with signed declarations assigning warranties to GIZ and project partners. Free replacement at the installation site (Nigeria) if performance falls below specifications.
| Please specify: | Brand name, model, type
Data sheet
5 | Battery
| Lithium-ion-battery LFP Battery, min. 5.37 kWh, 1C or 0.5C Rated. 100 systems + 10% spare units Note: 100 BESS units correspond to 100 project sites. Recommend 10% spare/replacement allocation. Scalable rack sizing per site as per site-specific BESS capacity in attached schedule. | 8,000 cycles @STC(75% Residual Capacity) DoD, Galvanized scalable battery racks and connection cables. Proof of conformity to IEC 61427, 62619, 63056 is required. Service life according to EUROBAT min. 12 years warranty at 20°C The battery must be supplied with its rack certified by the manufacturer. Proof of quality assurance system according to ISO 9001 / ISO 14001 ISO 45001 occupational health and safety or equivalent certification Fully insulated, corrosion-free lead terminal Fully insulated copper connectors and screw heads Interconnection lead poles with torque 20 - 22 Nm Environmentally friendly, min. 98 % recyclable Round-trip energy efficiency ≥ 95% Ampere-hour efficiency > 90% Self-discharge less than 2-3%/month at 20°C No memory effect Sufficiently large containers for electrolyte circulation Each battery is labelled with at least the following data: Manufacturer, type, model number, nominal voltage in V, nominal capacity in Ah/kWh, month and year of commissioning. Each cell must have a factory serial number. Standard battery accessories comprising current cable kit, communication cable, parallel connectors, racks, breakers, fuses and protection devices etc. The storage must be integrated and preconfigured as All in unit with other components. The battery must be scalable up to minimum 3 times initial capacity IEC 62759-1 shall be observed with regard to delivery and shipping requirements Must comply with IEC 62619, IEC 63056, UL 9540A, IEC62056, IEC 61000-6-2/4, ISO 4180 This item must be compatible with the inverter system and integrated in a water proof cabinet for outdoor installation.
| Charge regulator/ inverter-charger | The inverter/charger shall be suitable for off-grid or hybrid off-grid/grid-tied operation as applicable to each site. It shall incorporate integrated MPPT charge control (MPPT tracking efficiency ≥99%). Battery charge and discharge management shall be performed by the integral BMS of the LFP BESS in coordination with the inverter EMS. The inverter/charger shall support AC coupling with a backup diesel generator: single-phase 230 VAC for systems ≤15 kWp; three-phase 400 VAC for systems >15 kWp. Electrical conversion efficiency: ≥93% (systems ≤15 kWp); ≥96% (systems >15 kWp). Integrated data logging with ≥90-day local storage; remote monitoring via GSM/4G or Ethernet, PROSPECT-platform compatible. Remote monitoring is a mandatory requirement. Compliance with EN 62109-1 and IEC 62040-3 (UPS/off-grid inverter performance).
Supported battery types: Li-Ion, LFP Charge control: IUoU with automatic full and equalisation charging Protection of the battery against deep discharge, (current-dependent final discharge voltage) Protection of the battery against overcharging Regular equalisation charge (e.g. regular increase of the final charge voltage) Display of switch-off due to deep discharge and other reasons Battery voltage display (e.g. via LED) External battery temperature sensor included in the scope of delivery Low overvoltage with inductive and capacitive loads (please specify value) Permissibility of half-wave operation caused by power reduction with diode, e.g. hair dryer Compliance with EMC limits according to EN 55032 and EN 61000-3-2/3-3 ISO certification of the manufacturer is available
Protection functions: Short-circuit proof Overload protection Overtemperature protection Lightning and overvoltage protection AC side Compliance with other VDE/IEC regulations (contact protection etc.) Compliance with EMC limits (electromagnetic compatibility) according to EN 55032 and EN 61000-3-2/3-3 Radio interference suppression (VHF) Output power control of the feed-in inverter (item 1.3) via frequency for overcharge protection of the battery Other normative requirements IEC 62093 ;DIN EN 50178 ; are fulfilled CE declaration of conformity by the manufacturer is available. Confirmation by a conformity assessment body in accordance with ISO/IEC 17021 is available. CE marking of the battery-charging inverter is available. The battery charging inverters are marked accordingly. Communication interface: mandatory. RS485 (Modbus RTU), CAN bus, or Ethernet (Modbus TCP) interface required for integration with EMS/microgrid controller and remote monitoring platform (PROSPECT-compatible). Control cable for RS485/Modbus communication between battery BMS, inverter, and EMS controller: LIYCY paired 2×2×0.25 mm² screened twisted-pair or equivalent, to be provided where hardwired communication is used. Maximum run length 1,200 m at this cable spec (120 Ω termination resistors required at both ends). Where wireless communication is proposed as an alternative, the bidder must demonstrate equivalent reliability and provide a minimum 5-year warranty on the wireless communication hardware.
6 | Cable
| Solar cables | 1x 6 mm² copper cable (string runs ≤30 m) / 1x 10 mm² copper cable (DC home-run cables to combiner boxes — confirm per site-specific cable schedule) with double insulation for up to 1000V, type C2 (high flame resistance), AN3 (high UV resistance) Maximum permissible conductor temperature at least 90°C in continuous use. The standard EN 50618 is fulfilled. Please calculate cable lengths and diameters for a fully functional system operation. Solar DC wiring must be carried out in accordance with IEC 62930:2017. Maximum permissible conductor temperature at least 90°C in continuous use. The standard EN 50618 is fulfilled. Wooden drum of 500m each Please calculate cable lengths and diameters for a fully functional system operation. Solar DC wiring must be carried out in accordance with IEC 62930:2017. Solar cables shall be used from PV modules junction boxes up to converters incoming sections (MPPT) and must have the below listed minimum technical characteristics: · Maximum continuous operating temperature: 120 °C · Rated voltage (U0/U): 0,6/1 kV AC · Maximum DC voltage ≥ 1500 V DC · EPR insulated cables · UV resistant · Suitable for outdoor and underground installation European (EN), IEC and national (DIN VDE) must be fufilled
| DC Cables | Please calculate cable lengths and diameters for a fully functional system operation. Solar DC wiring must be carried out in accordance with IEC 62930:2017. European (EN), IEC and national (DIN VDE) must be fufilled
| AC Cables | Bidder shall calculate cable cross-sections and lengths per site based on: maximum voltage drop ≤3% under full load (IEC 60364-5-52); current-carrying capacity per installation method (IEC 60364-5-52 Table B.52); short-circuit withstand per IEC 60909. Cable schedule to be submitted as part of the technical bid.
| Empty conduits | PE cable conduits for burial, double wall (corrugated outside, smooth inside according to standard NF EN 50086-2-4)
| Other Components | UV-resistant cable ties in all necessary sizes and quantities. All earthing accessories required for the proper earthing of the system.(Please see NESIS Regulation 2015 Chapter 11) Power distribution/Switch cabinet should be fitted in the outdoor cabinet housing the entire system
| Accessories and spares | All accessories for proper fastening of the cables under the modules for the entire installation. 5% PV capacity Extra MC4 connectors, fuses, and bypass diodes on-site as part of spares inventory DC Connector (MC4) Specifications: - Protection Class: IP68 (weatherproof for Nigeria’s humid conditions). - Protection Type: UV-resistant, flame-retardant. - Rated Current: 30 A. - Contact Resistance: ≤0.5 mΩ. - Rated Voltage: 1500 V DC. - Fuses: • Type: PV-specific, gPV fuses. • Rated Current: 15 A. • Rated Voltage: 1500 V DC. • Breaking Capacity: 50 kA. - Bypass Diodes: • Type: Schottky diodes. • Rated Current: 15 A. • Rated Voltage: 45 V. • Junction Temperature: -40°C to +85°C
7 | Documentation
| The following documentation, in English, must be supplied in electronic form for all components of the system after the order has been placed: | Assembly instructions for the entire system. Overview for an installer on site, showing which components are connected to each other and how. This overview also refers to the corresponding installation instructions and assembly instructions for the individual components.
Circuit document
Description of the components
Wiring diagrams
Assembly instructions, installation instructions
Commissioning instructions
Operating instructions
Maintenance instructions
Error analysis and troubleshooting suggestions in the event of a malfunction
All necessary import papers like certificates of origin, detailed component catalogue, SONCAP (for each item), packing list (indicating component HS codes and Country of Origin), proforma invoice and any other document as may be required for Cutoms clearance. Mandatory blockchain-based component tracking Mandatory QR codes on every module linking to test data Original test reports Mandatory Factory witness testing for major components
8 | Material Delivery CIF Apapa Seaport
All material must be delivered CIF Apapa Seaport in Lagos (Nigeria) latest 3 months after order.
Immediately after placing the order, all relevant customs documents, such as the delivery note, packing list and pro forma invoice, must be submitted so that GIZ can prepare for import. This import preparation can take several months. Therefore the loading onto the ship can start only after approval by GIZ. This will happen when all customs documents are ready. The bidder must therefore allow to store all the goods for several months before transport can begin in the country of manufacture. The offer must include 3 months of storage at no additional cost. The costs for each additional month beyond the initial 3-month period must be specified as an option price for each additional month, up to a maximum of 9 additional months (total maximum storage period: 12 months). The storage period of 3 months will be part of the criteria for the evaluation. Please also note that the payment terms are linked to this.
| Please specify: | Dimensions (L×W×H) and gross weight (kg) including packaging for sea shipment shall be declared by the bidder for each major component type (PV modules per pallet, inverter per crate, BESS per unit, mounting structure per bundle
9a | Customs clearance (by giz)
| Customs clearance (by giz) | Customs clearance in Nigeria will be done by giz. All necessary import papers like certificates of origin, detailed component catalogue, SONCAP (for each item), packing list (indicating component HS codes and Country of Origin), proforma invoice, delivery note and other documents that may be required from the supplier for the Importation and Clearing via Nigeria Ports"
9b | Domestic Material Transport (by giz)
| Domestic Material Transport (by giz) | Domestic transport in Nigeria will be done by giz.
10 | Service on site (by Giz partner)
The installation will be done by giz and its partners. The bidder has to provide before the shipment for ALL items and components: - all documents mentioned in position 9 including assembly instructions, etc. - datasheets or technical descriptions - latest Software versions where applicable - manuals - building instructions - manufacturer warranties with assignment declarations by the manufacturer
The bidder shall provide a webinar of min. 3 days (3x4 hours) with the content of the demonstration of the full layout (planned), electrical components and the installation of all electrical components and the entire system (including assembly instruction). As well as operation and maintenance of the PV system incl. usage of the monitoring system. The webinar should take place during the shipment All work steps of the installation will be documented in detail (incl. the wiring diagram of all components and the PV-System).
Installation and commissioning of all components and the complete PV-System will be done by giz and its partners. The biddershall give full remote support and supervision (via video call) for all related electrical works regarding installation and commissioning of all delivered components and for the proper operation of the supplied technological equipment. Installation and commissioning at each site must be conducted according to Nigeria electrical quality and safety norms and standards. Remote support and supervision of the commissioning of the PV-System incl. function tests and trial operation.
The remote installation and supervision support shall be completed latest 1 - 12 months after the announcement of the successful customs clearance by the giz. Timeline will be communicated to the supplier (OEM) during implementation and depending on the local construction company.
At least 4 hours per system should be planned for the remote supervision and support. Please quote in total for up to 10 days (each day 4 hours) in your offer for remote support and supervision. The bidder is obliged to submit accordingly a time report. In case more support is needed, please provide your daily rate in the offer.
12 | Warranty
| min. 8 years | On all items and components. Fully according to GIZ General Purchase Conditions (GPC) 2023. The claims arising from the product and system warranties apply in addition to the claims for defects in accordance with GIZ GPC 2023. For individual components, longer warranty periods apply if described. Note: The 8-year minimum system warranty applies to workmanship and installation quality. Individual component product warranties as specified in Sections 2–5 apply in addition and supersede the system warranty for the respective components.
| Place of validity | All guarantee and warranty conditions apply free of charge CIF Lagos Nigeria.
| Guarantee assignment declarations | All warranties must be assigned to GIZ and project partners by declaration. This declaration must be signed and stamped by each manufacturer.

## Site-Specific Capacities
NISHP — Site-Specific System Capacities (5 States, 100 Sites) | [7 empty] | Ground conditions: Approximate details regarding pile depths and ground conditions are available. These can be sent on request, subject to a confidentiality undertaking. Please send an informal message via the procurement portal.
Total: 2,500 kWp Solar PV ¦ 6,300 kWh BESS ¦ 98 Systems across Akwa Ibom, Plateau, Enugu, Abia, Ogun
S/N | State | PHC / Facility | GPS Coordinates | Connected Load (kW) | Daily Energy (kWh) | Solar PV (kWp) | BESS (kWh)
AKWA IBOM ¦ 20 sites ¦ 500 kWp PV ¦ 1,260 kWh BESS
1 | Akwa Ibom | Cold Chain Store | 5.018506, 7.903533 | 7.522 | 58.652 | 120 | 300
2 | Akwa Ibom | HC Edo Esit Eket | 4.646827, 8.019473 | 4.5 | 37.76 | 24 | 60
3 | Akwa Ibom | HC Ibiaku Issiet | 4.942457, 8.009666 | 0.52 | 5.44 | 12 | 30
4 | Akwa Ibom | HC Okopedi | 4.844373, 8.128991 | 7.705 | 60.52 | 30 | 90
5 | Akwa Ibom | HP Idua Assang | 4.826242, 8.233629 | 0.26 | 1.86 | 12 | 30
6 | Akwa Ibom | PHC BASE, ABAT | 4.622293, 7.861014 | 8.37 | 63.05 | 24 | 60
7 | Akwa Ibom | PHC Base, Ikpa Ibekwe | 4.622363, 7.861871 | 2.897 | 12.892 | 12 | 30
8 | Akwa Ibom | PHC Adiasim | 5.074573, 7.700011 | 2.93 | 22.85 | 12 | 30
9 | Akwa Ibom | PHC Afaha Offiong | 4.871334, 7.910632 | 6.699 | 43.537 | 24 | 60
10 | Akwa Ibom | PHC Ibong Otoro Abak | 5.103588, 7.788398 | 2.745 | 21.68 | 12 | 30
11 | Akwa Ibom | PHC Idung Inang | 4.668284, 7.949034 | 5.76 | 38.2 | 24 | 60
12 | Akwa Ibom | PHC Iko Town | 4.524993, 7.774440 | 3.13 | 21.84 | 24 | 60
13 | Akwa Ibom | PHC Ikot Akpa Ukuk | 4.874171, 7.564842 | 6.33 | 28.2 | 12 | 30
14 | Akwa Ibom | PHC Ikot Edibon | 4.770909, 7.927780 | 12.23 | 84.56 | 50 | 120
15 | Akwa Ibom | PHC Ikot Esen Oku | 4.841954, 7.852265 | 3.265 | 26.48 | 12 | 30
16 | Akwa Ibom | PHC Ikot Eyo | 4.762101, 7.971727 | 3.993 | 30.484 | 12 | 30
17 | Akwa Ibom | PHC Ikot Ibritam | 4.844750, 7.744575 | 9.637 | 57.122 | 24 | 60
18 | Akwa Ibom | PHC Mbak Atai | 5.171866, 8.002029 | 0.4 | 3.2 | 12 | 30
19 | Akwa Ibom | PHC Odoro Ikpe | 5.355564, 7.745914 | 5.89 | 43.12 | 24 | 60
20 | Akwa Ibom | PHC Upenekang | 4.574560, 7.974290 | 7.595 | 39.855 | 24 | 60
PLATEAU ¦ 20 sites ¦ 500 kWp PV ¦ 1,260 kWh BESS
21 | Plateau | PHC Dorowa Tsoho | 9.526214, 8.984736 | 0.79 | 7.92 | 6 | 15
22 | Plateau | PHC Mista Ali | 10.03765, 8.849880 | 2.2 | 18.22 | 12 | 30
23 | Plateau | PHC Zandi | 9.846031, 9.251328 | 7.5 | 38.02 | 15 | 40
24 | Plateau | PHC Gangare | 9.913001, 8.895391 | 3.34 | 26.14 | 12 | 30
25 | Plateau | PHC Farin Lamba | 9.821394, 8.852186 | 9.23 | 96.4 | 50 | 120
26 | Plateau | PHC Riyom | 9.641529, 8.760418 | 3.79 | 9.44 | 12 | 30
27 | Plateau | PHC Bum | 9.691452, 8.639120 | 5.8 | 28.72 | 12 | 30
28 | Plateau | PHC Bokos | 9.298562, 8.997038 | 9.38 | 45.76 | 24 | 60
29 | Plateau | PHC Kwalmiya | 9.560609, 9.949816 | 4.21 | 26.12 | 12 | 30
30 | Plateau | PHC Kabwir | 9.391310, 9.563323 | 16.888 | 192.824 | 100 | 270
31 | Plateau | PHC Kadunu | 9.680529, 9.150305 | 0.39 | 2.64 | 6 | 15
32 | Plateau | PHC Ampang West | 9.3042328, 9.18713 | 19.11 | 52.21 | 30 | 70
33 | Plateau | PHC Fier | 9.406734, 9.399192 | 4.3 | 30.98 | 15 | 40
34 | Plateau | PHC Pilgani | 9.193062, 9.874039 | 5.87 | 80.7 | 40 | 75
35 | Plateau | PHC Nyer | 8.893889, 9.809396 | 1.198 | 7.748 | 6 | 15
36 | Plateau | PHC Sabongida | 8.739286, 9.743063 | 2.22 | 8.02 | 12 | 30
37 | Plateau | PHC Tunkus | 9.023095, 9.614898 | 2.79 | 18.72 | 12 | 30
38 | Plateau | PHC Lardang | 9.046652, 9.248200 | 2.04 | 15.36 | 12 | 30
39 | Plateau | PHC Kawo | 8.841826, 9.629530 | 16.08 | 207.76 | 100 | 270
40 | Plateau | PHC Yola Wakat | 9.154746, 9.989493 | 2.01 | 15.76 | 12 | 30
ENUGU ¦ 29 sites ¦ 500 kWp PV ¦ 1,260 kWh BESS
41 | Enugu | Affa Type 2 PHC | 6.601288, 7.324509 | 1.8 | 14.4 | 6 | 15
42 | Enugu | Aguobu Owa 1 (Ozomu) | 6.374863, 7.265560 | 0.08 | 0.96 | 6 | 15
43 | Enugu | Imezi Owa 1 (Umu-dioha) | 6.371817, 7.335458 | 0.96 | 8.72 | 6 | 15
44 | Enugu | Neke Oghe 3 | 6.441552, 7.316552 | 0.47 | 3.72 | 6 | 15
45 | Enugu | Obeleagu Umanna | 6.442852, 7.369343 | 0.43 | 3.72 | 6 | 15
46 | Enugu | Obuagu Mpu PHC | 6.100060, 7.610575 | 0.575 | 4.65 | 6 | 15
47 | Enugu | Obugo Adogbalato Type 2 PHC | 6.069065, 7.484397 | 1.2 | 10.2 | 6 | 15
48 | Enugu | Oghe II (Ihuonyia) | 6.485926, 7.248961 | 0.5 | 6 | 6 | 15
49 | Enugu | Ovoko Health Centre | 6.894003, 7.447664 | 0.42 | 3.48 | 6 | 15
50 | Enugu | Ugbowa-Owa Type 2 | 6.479920, 7.479181 | 1.59 | 12.92 | 6 | 15
51 | Enugu | Umuchigbo Type 2 PHC | 6.496653, 7.522685 | 0.59 | 4.2 | 6 | 15
52 | Enugu | Umurah PHC | 6.029377, 7.562810 | 0.71 | 4.92 | 6 | 15
53 | Enugu | Agbani Health Centre | 6.309533, 7.554138 | 2.94 | 21.88 | 12 | 30
54 | Enugu | Aguobu Owa II Ezi-owa | 6.380218, 7.258446 | 2.64 | 18.52 | 12 | 30
55 | Enugu | GRA West | 6.429146, 7.491655 | 2.94 | 17.64 | 12 | 30
56 | Enugu | Mburubu Type 2 HC, Nkanu East LGA | 6.173440, 7.634785 | 2.38 | 16.08 | 12 | 30
57 | Enugu | Ngwo Asaa PHC | 6.298016, 7.370520 | 2.75 | 21.58 | 12 | 30
58 | Enugu | Ogui Nike Health Centre | 6.448477, 7.508676 | 2.37 | 18.96 | 12 | 30
59 | Enugu | Olo/Amagu/Umulokpa 1 Amandium | — | 1.94 | 21.04 | 12 | 30
60 | Enugu | Type 2 PHC Ette Central | — | 2.94 | 26.64 | 12 | 30
61 | Enugu | Udunedem Eke Igugu PHC | 6.888515, 7.492500 | 3.67 | 25.14 | 12 | 30
62 | Enugu | Amaja Health Center | — | 4.285 | 36.8 | 24 | 60
63 | Enugu | Edem Type 2 PHC | 6.518981, 7.514278 | 9.62 | 53.34 | 24 | 60
64 | Enugu | Ihe Agu Nru Nsukka Type 2 PHC | 6.799963, 7.418684 | 5.42 | 33.84 | 24 | 60
65 | Enugu | Nsukka Health Centre | 6.883036, 7.480571 | 5.43 | 39.36 | 24 | 60
66 | Enugu | Umumba Type 2 PHC, Achi Agu 3 | — | 7.394 | 41.88 | 24 | 60
67 | Enugu | Ugwuomu Type 2 PHC | 6.496653, 7.522685 | 10.49 | 84.2 | 50 | 120
68 | Enugu | Umuenwene Type 2 PHC | 6.499933, 7.519140 | 10.635 | 120.37 | 50 | 120
69 | Enugu | Emene Type 2 PHC | 6.469658, 7.583122 | 11.746 | 121.818 | 100 | 270
ABIA ¦ 12 sites ¦ 500 kWp PV ¦ 1,260 kWh BESS
70 | Abia | Ndiolumbe | 5.520209, 7.491600 | 3.2 | 25.6 | 12 | 30
71 | Abia | Amaekpu | 5.644275, 7.836442 | 4.5 | 23.87 | 12 | 30
72 | Abia | Aba Cottage Hospital Abayi | 5.133932, 7.335797 | 9.455 | 80.13 | 24 | 60
73 | Abia | Ahiabaubi | 5.390706, 7.349511 | 13.592 | 71.596 | 24 | 60
74 | Abia | Owerrinta | 5.301996, 7.293037 | 6.345 | 73.14 | 24 | 60
75 | Abia | Ekearo | 5.217505, 7.313199 | 7.06 | 77.93 | 24 | 60
76 | Abia | Ihie Obeaku | 5.023904, 7.314699 | 11.165 | 21.19 | 24 | 60
77 | Abia | Obulisi | 5.990467, 7.385447 | 6.195 | 71.94 | 24 | 60
78 | Abia | Nkporo Cottage Hospital | — | 80 | 150 | 32 | 90
79 | Abia | Ikwuano General Hospital | — | 130 | 300 | 100 | 250
80 | Abia | General Hospital Mgboko | — | 200 | 300 | 100 | 250
81 | Abia | PH_01 PHC | — | 6 | 10 | 10 | 20
82 | Abia | PH_02 PHC | — | 5 | 8 | 8 | 15
83 | Abia | Arochukwu General Hospital | — | 200 | 300 | 100 | 250
OGUN ¦ 17 sites ¦ 500 kWp PV ¦ 1,260 kWh BESS
84 | Ogun | Kugba Primary Health Centre | 7.174738, 3.356682 | 4.02 | 13.28 | 12 | 30
85 | Ogun | Olose Primary Health Care | 6.810811, 3.175563 | 4.198 | 24.946 | 12 | 30
86 | Ogun | Itoki Primary Health Care | 6.714862, 3.285583 | 8.132 | 29.224 | 12 | 30
87 | Ogun | Eruwon PHC | 6.838947, 3.965909 | 8.406 | 29.732 | 12 | 30
88 | Ogun | Ijebu Imushin Health Center | 6.798253, 3.990458 | 6.115 | 16.56 | 12 | 30
89 | Ogun | Sabo Aguda PHC | 6.832517, 3.647952 | 7.82 | 21.72 | 12 | 30
90 | Ogun | Ayetoro General Hospital | 7.231901, 3.011431 | 10.75 | 27.394 | 24 | 60
91 | Ogun | Ajegunle PHC | 6.673987, 2.769940 | 5.235 | 29.38 | 12 | 30
92 | Ogun | Ofada Primary Health Center | 6.863936, 3.426422 | 3.796 | 21.92 | 12 | 30
93 | Ogun | Odogbolu Ultra Modern PHC | 6.828829, 3.774525 | 1.435 | 5.51 | 12 | 30
94 | Ogun | Atapele PHC | 7.496922, 2.955147 | 2.39 | 8.68 | 12 | 30
95 | Ogun | Primary Health Care Center Ilara | 7.408254, 2.749751 | 6.176 | 21.468 | 12 | 30
96 | Ogun | Papalanto Health Clinic | 6.882963, 3.190854 | 5.967 | 39.814 | 24 | 60
97 | Ogun | Lomiro PHC | 6.495494, 4.420714 | 4.97 | 40.04 | 24 | 60
98 | Ogun | Odeda General Hospital | 7.235650, 3.526690 | 22.879 | 66.37 | 50 | 120
99 | Ogun | Isara General Hospital | 6.988669, 3.681498 | 30.531 | 92.204 | 120 | 300
100 | Ogun | Ibipe PHC | 6.940656, 3.920468 | 47.28 | 115.96 | 126 | 330
TOTAL — 5 STATES, 100 SITES | [5 empty] | 2518 | 6335