## Containerized DC
Technical Requirements for the containerized Data Center The Data Center (hereinafter referred to as the DC) shall be of a containerized design. The external dimensions of the container (L × W × H) max. 8000 × 3200 × 3000 mm. |  |  | The Tenderer is required to provide, for each item (row), the requested confirmations and the specific data, performance parameters, or information relating to the offered product in Column D. The Tenderer shall ensure that all entries are complete and accurate. Please note that any deviation from the Technical Specification (Statement of Requirements) or any missing information may result in the rejection of the tender. If the Tenderer considers that there are justified reasons for a deviation, a clarification request shall be submitted during the ongoing procurement procedure.
Nr. | Bezeichnung | Beschreibung
1 | External dimensions of the container | (L × W × H) max. 8000 x 3000 x 3000 mm | [Please enter the details here.]
Overview Containerized DC Components
2 | 6 x Server Racks | 19” server racks | [Please enter "Yes" to confirm the minimum requirement.]
3 | 2 x Power Distribution Units | At least 2 Power Distribution Units per each server rac (hereinafter referred to as PDUs) | [Please enter "Yes" to confirm the minimum requirement.]
4 | Hot aisle containment solution | Hot aisle containment solution | [Please enter "Yes" to confirm the minimum requirement.]
5 | 1 x Uninterruptible Power Supply | 1 unit Uninterruptible Power Supply (hereinafter referred to as UPS) with a capacity of not less than 40 kVA | [Please enter "Yes" to confirm the minimum requirement.]
6 | 1 x Air conditioning system (3 cooling units) | Air conditioning system – at least 3 cooling units with the ability to operate in an N+1 configuration | [Please enter "Yes" to confirm the minimum requirement.]
7 | 1 x Electrical distribution panel | Electrical distribution panel with the capability to connect two power supply lines (from the external power grid and from a generator) | [Please enter "Yes" to confirm the minimum requirement.]
8 | 1 x Fire detection and fire suppression system | Fire detection and fire suppression system | [Please enter "Yes" to confirm the minimum requirement.]
9 | 1 x Internal monitoring system (enviroment) | Internal container environment monitoring system | [Please enter "Yes" to confirm the minimum requirement.]
10 | 1 x Monitoring system (operating parameters of the engineering infrastructure) | System for monitoring the operating parameters of the containerized DC engineering infrastructure | [Please enter "Yes" to confirm the minimum requirement.]
11 | Lighting and emergency lighting | Lighting and emergency lighting | [Please enter "Yes" to confirm the minimum requirement.]
12 | 1 x Access control and management system (hereinafter referred to as ACMS) | Access control and management system (hereinafter referred to as ACMS) | [Please enter "Yes" to confirm the minimum requirement.]
13 | 1 x Video surveillance system | Video surveillance system | [Please enter "Yes" to confirm the minimum requirement.]
14 | 1 x Generator | Generator with a capacity of not less than 165 kVA and 72-hour autonomous operation | [Please enter "Yes" to confirm the minimum requirement.]
Detailed Requirements and Specifications
Requirements for the container structure
1.1 | Continuous 24/7 Operation | The data center must be designed to ensure continuous operation of IT equipment without on-site personnel supervision, operating 24/7. | [Please enter "Yes" to confirm the minimum requirement.]
1.2 | Container Construction | The DC design must provide that all IT equipment and all non-IT equipment, except of the external units of the air conditioning system and the generator, are installed inside the container | [Please enter "Yes" to confirm the minimum requirement.]
1.3 | Container Construction | The container structure must be fully welded | [Please enter "Yes" to confirm the minimum requirement.]
1.4 | Entrance Canopy | Canopy over the entrance door to protect from rain and snow
1.5 | Fire Protection | Fire resistance rating: EI30 | [Please enter "Yes" to confirm the minimum requirement.]
1.6 | Flooring Requirements | The internal floor surface of the container must have an antistatic coating | [Please enter "Yes" to confirm the minimum requirement.]
1.7 | Flooring Requirements | The floor covering in container walkways must be anti-slip | [Please enter "Yes" to confirm the minimum requirement.]
1.8 | Exterior Finish | The external surface of the container must be painted, and the color scheme must comply with the RAL6003 color palette | [Please enter "Yes" to confirm the minimum requirement.]
1.9 | Physical Security | The container must be equipped with a door system with burglary resistance level RC3 | [Please enter "Yes" to confirm the minimum requirement.]
1.10 | Physical Security | The door system must be fitted with an electric lock connected to an ACS (Access Control System) card reader | [Please enter "Yes" to confirm the minimum requirement.]
1.11 | Physical Security | After the electric lock has been released, the door shall open by means of a handle | [Please enter "Yes" to confirm the minimum requirement.]
1.12 | Emergency Egress | The door system shall allow personnel to leave the data center during an alarm even when the door is locked by means of panic hardware (anti-panic exit device) | [Please enter "Yes" to confirm the minimum requirement.]
1.13 | Cable and Utility Interfaces | The container must be equipped with a system of cable channels for connecting external cables and pipes | [Please enter "Yes" to confirm the minimum requirement.]
1.14 | Grounding | The container must have the capability to connect to the grounding busbars at two corners | [Please enter "Yes" to confirm the minimum requirement.]
Requirements for the server racks
2.1 | Rack standard | 19" | [Please enter the details here.]
2.2 | Rack height | 42 Units | [Please enter the details here.]
2.3 | Rack depth | At least 1200 mm | [Please enter the details here.]
2.4 | Protection rating | Not less than IP20 | [Please enter the details here.]
2.5 | Front and rear doors | Perforated metal | [Please enter "Yes" to confirm the minimum requirement.]
2.6 | Maximum (static) load capacity per rack | At least 12,000 N | [Please enter the details here.]
2.7 | Rack Layout and Airflow | Server racks in the container must be positioned to ensure front-to-back airflow through the installed equipment | [Please enter "Yes" to confirm the minimum requirement.]
Requirements for PDUs (Power Distribution Units)
3.1 | Power Supply | 3-phase | [Please enter the details here.]
3.2 | Power Supply Capacity | Allowable current: at least 3×16A | [Please enter the details here.]
3.3 | PDU Mounting Requirements | The PDU must be designed for fixed mounting in the rack | [Please enter "Yes" to confirm the minimum requirement.]
3.4 | Outlet Configuration and Power Monitoring | The PDU must be equipped with IEC 320 C13 and IEC 320 C19 outlets with individual outlet-level control and power measurement capabilities. | [Please enter the details here.]
Requirements for the “hot aisle” containment solution
4.1 | Hot Aisle Containment System | The container must include a physical containment system separating the “hot aisle” from the rest of the space | [Please enter "Yes" to confirm the minimum requirement.]
4.2 | Access Hot Aisle Containment | Entry to the “hot aisle” must be through sliding doors | [Please enter "Yes" to confirm the minimum requirement.]
Requirements for the UPS (Uninterruptible Power Supply)
5.1 | Total UPS capacity | At least 40 kVA | [Please enter the details here.]
5.2 | Power supply | 3-phase | [Please enter "Yes" to confirm the minimum requirement.]
5.3 | UPS design | Modular system | [Please enter "Yes" to confirm the minimum requirement.]
5.4 | Number of modules in the system | At least 3 modules with 2+1 redundancy capability | [Please enter "Yes" to confirm the minimum requirement.]
5.5 | Battery Configuration | Batteries may be installed either within the UPS itself or in separate external enclosures | [Please enter the details here.]
5.6 | Control Panel | Must include a control panel | [Please enter "Yes" to confirm the minimum requirement.]
5.7 | Network Monitoring Interface | Must include an SNMP card for connection to a monitoring system | [Please enter "Yes" to confirm the minimum requirement.]
5.8 | Battery Temperature Monitoring | Must support temperature measurement of batteries | [Please enter "Yes" to confirm the minimum requirement.]
Requirements for the Air Conditioning System
6.1 | Cooling System Type | Integrated precision air cooling system | [Please enter "Yes" to confirm the minimum requirement.]
6.2 | System Architecture | Modular split-system design | [Please enter "Yes" to confirm the minimum requirement.]
6.3 | Cooling Unit Configuration | Minimum 3/3 indoor and outdoor units | [Please enter "Yes" to confirm the minimum requirement.]
6.4 | Indoor Unit Placement | Indoor units installed in line with server racks | [Please enter "Yes" to confirm the minimum requirement.]
6.5 | Outdoor Unit Specification | Outdoor units with fan-controlled condenser, VFD compressor, electronic expansion valve | [Please enter the details here.]
6.6 | Cooling Technology | Indirect refrigerant cooling with inverter technology | [Please enter the details here.]
6.7 | Cooling Capacity | Cooling capacity ≥ 20 kW per unit | [Please enter the details here.]
6.8 | Airflow Performance | Air flow ≥ 4800 m³/h at 50 Hz | [Please enter the details here.]
6.9 | Remote Monitoring and Management | Ethernet/SNMP monitoring capability | [Please enter "Yes" to confirm the minimum requirement.]
6.10 | Maintainability / Hot-Swap Capability | Fan replacement during operation | [Please enter "Yes" to confirm the minimum requirement.]
6.11 | Temperature Regulation | Temperature control | [Please enter "Yes" to confirm the minimum requirement.]
6.12 | Fan Speed Control | Smooth regulation of outdoor unit fans | [Please enter "Yes" to confirm the minimum requirement.]
6.13 | Compressor Technology | Compressor with inverter control | [Please enter "Yes" to confirm the minimum requirement.]
6.14 | Operating Temperature Range | Operating temperature range of indoor units – 5 °C - 40 °C or better | [Please enter the details here.]
6.15 | Ingress Protection Rating (IP) | Ingress Protection (IP) rating according to EN 60529 – not lower than IP20 | [Please enter the details here.]
6.16 | Condensate Drainage System | Drainage pipes with automatic heating for condensate (3–5 m) | [Please enter the details here.]
Requirements for the Electrical Distribution Board
7.1 | Dual Power Input Configuration | Connection of two 3-phase power lines (external grid and generator) | [Please enter "Yes" to confirm the minimum requirement.]
7.2 | Power Source Switching | Automatic and manual switching between external power inputs | [Please enter "Yes" to confirm the minimum requirement.]
7.3 | UPS Integration | Connection of the UPS | [Please enter "Yes" to confirm the minimum requirement.]
7.4 | Lighting Power Supply | Connection of internal and emergency lighting | [Please enter "Yes" to confirm the minimum requirement.]
7.5 | Load Management | Load group management | [Please enter "Yes" to confirm the minimum requirement.]
7.6 | Lightning Protection | Kit for installing lightning protection | [Please enter "Yes" to confirm the minimum requirement.]
7.7 | Grounding System | Kit for installing grounding the container | [Please enter "Yes" to confirm the minimum requirement.]
Requirements for the Fire Detection and Suppression System
8.1 | Gas Fire Suppression System | Automatic autonomous gas fire suppression system for entire container volume | [Please enter "Yes" to confirm the minimum requirement.]
8.2 | Fire Protection Coverage | Protection of server racks and container areas | [Please enter "Yes" to confirm the minimum requirement.]
8.3 | Automatic System Activation | Automatic activation regardless of detection location | [Please enter "Yes" to confirm the minimum requirement.]
8.4 | Manual Activation and Control | Manual activation and control | [Please enter "Yes" to confirm the minimum requirement.]
8.5 | Fire Alarm Notification | Visual and audible alarms | [Please enter "Yes" to confirm the minimum requirement.]
8.6 | Fire Alarm System Integration | Connection to external fire alarm control panel | [Please enter "Yes" to confirm the minimum requirement.]
Requirements for the container internal environment monitoring system
9.1 | Monitoring System Overview | Monitoring system installed for internal container environment monitoring | [Please enter "Yes" to confirm the minimum requirement.]
9.2 | Sensor Integration and Expansion Capability | Connection of temperature/humidity, access, leakage and power sensors | [Please enter "Yes" to confirm the minimum requirement.]
9.3 | Communication Protocols | Supported protocols (TCP/IP, SNMP, SSH, FTP, Modbus, etc.) | [Please enter "Yes" to confirm the minimum requirement.]
9.4 | System Interfaces and Connectivity | Supported interfaces and physical connections (USB, Ethernet, RJ45, CAN bus, etc.) | [Please enter "Yes" to confirm the minimum requirement.]
9.5 | Network Management Integration | Connection to network management system via SNMP | [Please enter "Yes" to confirm the minimum requirement.]
9.6 | System Configuration and Management | System configuration via web/USB | [Please enter "Yes" to confirm the minimum requirement.]
9.7 | Alarm Notification and Reporting | Notifications via mail server | [Please enter "Yes" to confirm the minimum requirement.]
Requirements for the monitoring system of engineering infrastructure parameters of the container data center
10.1 | Real-Time Infrastructure Monitoring | Monitoring system for engineering infrastructure parameters in real time | [Please enter "Yes" to confirm the minimum requirement.]
10.2 | Integrated Infrastructure Management | Autonomous integrated system collecting data from non-IT infrastructure | [Please enter "Yes" to confirm the minimum requirement.]
10.3 | Power Infrastructure Monitoring | Monitoring of distribution switchboard power supply | [Please enter "Yes" to confirm the minimum requirement.]
10.4 | Cooling System Monitoring | Monitoring of air conditioning system | [Please enter "Yes" to confirm the minimum requirement.]
10.5 | Access Control System Integration | Integration of Access Control System (ACS) | [Please enter "Yes" to confirm the minimum requirement.]
10.6 | Rack Power Monitoring | Monitoring of PDU power supply in server racks | [Please enter "Yes" to confirm the minimum requirement.]
10.7 | Leak Detection Monitoring | Refrigerant leak detection monitoring | [Please enter "Yes" to confirm the minimum requirement.]
10.8 | Communication Protocol Support | Support for MODBUS, HTTP(S), DHCP, SNMP, FTP(S), etc. | [Please enter "Yes" to confirm the minimum requirement.]
10.9 | Control Logic and Programming Standard | Support for IEC 61131-3 programming languages | [Please enter "Yes" to confirm the minimum requirement.]
10.10 | System Expandability and Scalability | The system must allow expansion with additional input/output modules if modification/replacement/addition of certain non-IT infrastructure components of the data center is required in the future. | [Please enter "Yes" to confirm the minimum requirement.]
Requirements for lighting and emergency lighting
11.1 | General Lighting System | Ceiling-mounted LED lamps | [Please enter "Yes" to confirm the minimum requirement.]
11.2 | Lighting Control | Dedicated switches labeled "LIGHTING" | [Please enter "Yes" to confirm the minimum requirement.]
11.3 | Illumination Level | Average lighting intensity ≥ 500 lux | [Please enter the details here.]
11.4 | Emergency Lighting Backup | Emergency lighting with integrated battery backup | [Please enter "Yes" to confirm the minimum requirement.]
11.5 | Emergency Lighting Placement | Emergency lighting location above entrance door | [Please enter "Yes" to confirm the minimum requirement.]
11.6 | Emergency Evacuation Signage | Emergency lighting must indicate the direction of evacuation from the container room. | [Please enter "Yes" to confirm the minimum requirement.]
Requirements for the Access Control System (ACS)
12.1 | Physical Security System | Autonomous access control and security system for physical protection | [Please enter "Yes" to confirm the minimum requirement.]
12.2 | Access Authentication | Access via contactless card reader | [Please enter "Yes" to confirm the minimum requirement.]
12.3 | Card Reader Installation | External card reader installation near entrance | [Please enter "Yes" to confirm the minimum requirement.]
12.4 | Security Alarm and Event Notification | Alarm generation and notification upon access violation | [Please enter "Yes" to confirm the minimum requirement.]
12.5 | Access Control System Management | Remote ACS management via client software | [Please enter "Yes" to confirm the minimum requirement.]
Requirements for the Video Surveillance System
13.1 | Video Surveillance System Overview | Autonomous video surveillance system for visual inspection and event monitoring | [Please enter "Yes" to confirm the minimum requirement.]
13.2 | Camera Configuration and Coverage | Minimum number and location of cameras (hot aisle, cold aisle, entrance, outdoor) | [Please enter "Yes" to confirm the minimum requirement.]
13.3 | Power over Ethernet (PoE) Support | PoE-supported cameras | [Please enter "Yes" to confirm the minimum requirement.]
13.4 | Remote Monitoring Capability | Remote real-time monitoring by operators | [Please enter "Yes" to confirm the minimum requirement.]
13.5 | Video Data Storage | Local recording server inside container | [Please enter "Yes" to confirm the minimum requirement.]
13.6 | Video Playback and Data Analysis | Access to recorded data for event analysis | [Please enter "Yes" to confirm the minimum requirement.]
13.7 | Data Export and Transfer | Transfer of recorded data to another location | [Please enter "Yes" to confirm the minimum requirement.]
13.8 | System Expandability | Connection of additional cameras | [Please enter "Yes" to confirm the minimum requirement.]
13.9 | Camera Resolution | Maximum camera resolution ≥ 32 MP | [Please enter the details here.]
13.10 | Network Bandwidth Capacity | Total camera data stream >100 Mbps | [Please enter the details here.]
Requirements for the Generator
14.1 | Generator System Overview | Generator as backup power source | [Please enter "Yes" to confirm the minimum requirement.]
14.2 | Generator Technical Specifications | Stationary, 3-phase, 400 V, 50 Hz, 132 kW, 165 kVA, diesel | [Please enter the details here.]
14.3 | Generator Functional Features | AVR, fuel indicator, oil monitoring, starter battery, controller, emergency stop | [Please enter "Yes" to confirm the minimum requirement.]
14.4 | Generator Installation Requirements | Installation on vibration-isolated frame | [Please enter "Yes" to confirm the minimum requirement.]
14.5 | Acoustic Enclosure and Physical Protection | Soundproof and lockable canopy | [Please enter "Yes" to confirm the minimum requirement.]
14.6 | Fuel Storage and Extended Runtime | Additional external fuel tank for >72 h autonomy | [Please enter the details here.]
14.7 | External Fuel Tank Requirements | External fuel tank specifications | [Please enter "Yes" to confirm the minimum requirement.]
14.8 | Installation Location Requirements | Separate installation 20–30 m from container | [Please enter "Yes" to confirm the minimum requirement.]
14.9 | Power Connection Cables | 30m cable for connecting the generator to the container | [Please enter the details here.]
14.10 | Power Connection Cables | 50m cable for connecting the container to the external power grid (dual power inputs). | [Please enter the details here.]

## Tabelle2
Yes
No

## Tabelle1 (hidden)
| PV Plant Equipment | Unit | Quantity
1 | Solar Panels (Photovoltaic) | piece | 144
2 | Inverter Units
| 50 kW Inverter | piece | 1
| Steel Inverter holder (Concrete roof) | piece | 1
3 | Data Logger &Scada Systems | set | 1
| SCADA SYSTEM | set | 1
4 | Cables, Connectors Cable Trays and Wiring | set | 1
5 | Protection, Switchgear Materials, Relays, Panels and Meters | set | 1
6 | Grounding | set | 1
7 | Supporting Construction | set | 133
8 | Roof Anchors for Work Safety (Min.!) | piece | 3
9 | Grid Connection and Transformer | lump sum | 1
10 | Counters, MV Cells and Relays | set | 1
11 | Fire Extinguisher Tube | piece | 5
12 | Emergency Stop Button | piece | 1
13 | Stainless Steel Signboard ca. 1000x400x30/50mm | piece | 1
14 | Fire Escape (optional!) To be planned, only if requested by the TEDAŞ-ENERJISA Commission | lump sum | 1
Sum Material Supply
| PV Plant Equipment | Unit | Quantity
15 | Structural System Assembly | lump sum | 1
16 | Electrical System Assembly&Installation | lump sum | 1
17 | Physical Control | lump sum | 1
18 | Material Supply DAP on each Site | lump sum | 1
19 | Commissioning | lump sum | 1
20 | Connection to the grid | lump sum | 1
21a | Maintenance for the first year after provisional acceptance | lump sum | 1
21b | Maintenance for the second year after provisional acceptance (optional!) | lump sum | 1
22 | "All risk" Insurance (covering indemnity insurance) | lump sum | 1
Sum Services