Technical Specifications for the UPS

- Three-phase Online Double Conversion UPS.

- Minimum rated capacity: 40 kVA (or equivalent solution duly justified by the supplier) The UPS system shall be designed to support a maximum load capacity of approximately 21.5 kW (measured load), with a design margin bringing the required capacity to approximately 32 kW equivalent, corresponding to a 40 kVA three-phase UPS system.)

- Power factor: ≥ 0.9.

- Minimum autonomy: 30 minutes at the designed load.

- Battery technology: Lithium batteries.

- Integrated maintenance bypass.

- Protection against overvoltage, undervoltage, overload, and short circuits.

- LCD display and monitoring interface.

- SNMP/Web-based remote monitoring capability.

- Scalable and expandable architecture for future capacity increases.

- Automatic Transfer Switch (ATS) for seamless transfer to the backup power source.

- External battery bank sized to provide the required autonomy.

- Surge Protection Devices (SPD) and dedicated circuit breakers.

- Proper grounding and earthing system in compliance with applicable standards. The requirement refers primarily to IEC 60364 (Low-voltage electrical installations) and IEC 61140 (Protection against electric shock).

- Load balancing across phases.

- Noise level: max. (69 dBA at 7m)

- Input voltage: 400 V AC (three-phase) an Output voltage: 400/230 V AC

- Efficiency: Online Double Conversion technology, Efficiency of at least 95% in online mode (Higher efficiency solutions may be proposed and shall be clearly indicated by the supplier).

- Climatic conditions: Ambient temperature: 15°C to 35°C, Relative humidity: up to 90% non-condensing, Indoor installation, Dust levels corresponding to a standard office environment. The supplier shall specify any additional environmental requirement)

- Relevant norms: IEC 60364, IEC 61140, IEC 62040-1, IEC 62040-2, IEC 62040-3, IEC 62305, ISO 9001. The supplier shall provide evidence of compliance with the applicable standards.

Compatibility with the existing backup power system (generator):

- Model: GE.PK.110100.PRO+011
- Engine brand : PERKINS
- Serial Number: 45277
- Rated Power: 100 kVA
- Rated Active Power: 80 kW
- Power Factor (Cos φ): 0.8
- Output Voltage: 400/230 V
- Current: 144.51 A
- Frequency: 50 Hz
- Speed: 1500 RPM
- Manufacturing Date: 05/08/2024
- Origin: Made in Europe