ANNEX 2

DETAILED FACILITY DESCRIPTION FOR SELECTED PUBLIC EMPLOYMENT CENTERS (PECs)

| Programme: | Joint Action “Jobs, Migration and Development (JMD) |
| --- | --- |
| PN: | G-018152-005.00 |
| Title of Work: | Design, Procurement & Installation of Solar PV systems at 8 selected Public Employment Centers (PECs) |

# A

# FACILITY DESCRIPTION

Facility Name: Wenchi PEC

Facility Type: Building Structure

Location: Wenchi in the Bono Region (7°44′38.6″N, 2°06′01.8″W)

Wenchi PEC building is an old single-storey masonry facility shared with another institution. No structural upgrades have been performed. The PV system proposed is 6 kWp covering 26.5 m² roof area.

# ROOF STRUCTURE AND FIELD OBSERVATION

The roof is a monopitch timber rafter system pitched at 5.5°. The rafters are spaced at 1150mm centres, with cross-sectional dimensions of 100mm depth × 50mm width, spanning a projected distance of 4.2m. Purlins with size of 75mm depth x 50mm width and spacing of 1100mm centres are used as secondary members to provide inermediate support for the roof covering. Pictorial representation of the as-built roof is shown in Figure 1.

Figure 1: Wenchi Roof Plan and Typical Section

The on-site survey indicated that the rafters and purlins are in good condition, with no signs of distress or deterioration. The spans, spacing, and member sizes are considered reasonable and typical of local construction practice. The building appears structurally sound and robust with no visible cracks. Site photographs are presented in Figure 2.

Figure 2: Wenchi Site Pictures

# IDENTIFICATION OF MOUNTING AREAS AND FIXING MEMBERS

Rafters were found to be the most suitable fixing members, owing to their stiffness, direct load path, shorter spacing, and ease of access. Figure 3 shows the usable roof regions and proposed fixing members. The usable rooftop area available (32.0m2) is sufficient to accommodate the capacity of the proposed solar PV system.

Figure 3: Wenchi Suitable Spaces for the PV Installations

# VERIFICATION OF ROOF STRUCTURAL CAPACITY

The structural evaluation confirmed that all assessed roof members possess sufficient capacity to accommodate the demands from the proposed roof-top solar PV system. The combined effects of gravity and wind loads were found to be within acceptable limits. Accordingly, the roof can be considered structurally adequate for the safe installation of the proposed roof-top solar PV system, provided that anchoring and mounting are executed in line with the recommended fixing members and good engineering practice.

# TECHNICAL SPECIFICATION FOR MOUNTING

The following requirements ensure safe and structurally sound installation of the proposed roof-top PV system:

- Mount PV modules flush with the roof slope, maintaining a standoff < 300 mm, and place them within central roof zones identified in Appendix A (avoiding edges, corners, and overhangs).

- Fix rails directly to rafters, with rail spacing and anchor spacing each not exceeding 1.0 m, to ensure uniform distribution of PV and wind loads on rafters.

- Design anchorage for an unfactored uplift pressure of 1.0 kN/m².

- Use corrosion-resistant mounting components (galvanised steel, aluminium, or stainless steel), and isolate dissimilar metals to prevent galvanic corrosion.

- Seal all roof penetrations to maintain watertightness.

- Avoid stacking modules or concentrating installers at a single location to prevent temporary overloading of roof members.

- Any deviation from the specified fixing members or mounting zones requires prior structural approval, and works shall be supervised by client appointed supervisor to ensure compliance.

# APPENDIX A: ROOF AS-BUILT DRAWINGS AND RECOMMENDED MOUNTING REGIONS / FIXING MEMBERS

B

# FACILITY DESCRIPTION

Facility Name: Asante Bekwai PEC

Facility Type: Building Structure

Location: Asante Bekwai in the Ashanti Region (6°27′21.3″N, 1°34′55.5″W)

The Asante Bekwai PEC is an old masonry building with block walls supporting the roof. The roof structure was reconstructed in 2024, enhancing the building’s structural integrity. The PV system planned is 6 kWp over 26.5 m² roof area.

- ROOF STRUCTURE AND FIELD OBSERVATION

The hipped roof pitched at 45°, is formed with a strutted ridge-supported rafter system constructed of timber. The rafters, which span a projected length of 2.7m, have cross-sectional dimensions of 75mm depth × 50mm width, spaced uniformly at 900mm centres. Strutting beams, measuring 100mm depth × 50mm width, provide intermediate support and span approximately 3m. Purlins with size of 50mm depth x 75mm width and spacing of 950mm centres are present to support the roof covering and provide continuity. Pictorial representation of the as-built roof is shown in Figure 1.

Figure 4: Asante Bekwai Roof Plan and Typical Section

The survey indicated that the roof members are in good condition, with no visible deterioration or signs of distress. The building is robust, and no cracks, visible deformations, or distresses of structural concerns were observed. Site photographs are presented in Figure 2.

Figure 5: Asante Bekwai Site Pictures

- IDENTIFICATION OF MOUNTING AREAS AND FIXING MEMBERS

Rafters were found to be the most suitable fixing members, owing to their stiffness, direct load path, shorter spacing, and ease of access. Figure 3 shows the usable roof regions and proposed fixing members. The usable rooftop area available (31.0m2) is sufficient to accommodate the capacity of the proposed solar PV system.

Figure 6: Asante Bekwai Suitable Spaces for the PV Installations

- VERIFICATION OF ROOF STRUCTURAL CAPACITY

The structural evaluation confirmed that all assessed roof members possess sufficient capacity to accommodate the demands from the proposed roof-top solar PV system. The combined effects of gravity and wind loads were found to be within acceptable limits. Accordingly, the roof can be considered structurally adequate for the safe installation of the proposed roof-top solar PV system, provided that anchoring and mounting are executed in line with the recommended fixing members and good engineering practice.

- TECHNICAL SPECIFICATION FOR MOUNTING

The following requirements ensure safe and structurally sound installation of the proposed roof-top PV system:

- Mount PV modules flush with the roof slope, maintaining a standoff < 300 mm, and place them within central roof zones identified in Appendix A (avoiding edges, corners, and overhangs).

- Fix rails directly to rafters, with rail spacing and anchor spacing each not exceeding 1.0 m, to ensure uniform distribution of PV and wind loads on rafters.

- Design anchorage for an unfactored uplift pressure of 1.0 kN/m².

- Use corrosion-resistant mounting components (galvanised steel, aluminium, or stainless steel), and isolate dissimilar metals to prevent galvanic corrosion.

- Seal all roof penetrations to maintain watertightness.

- Avoid stacking modules or concentrating installers at a single location to prevent temporary overloading of roof members.

- Any deviation from the specified fixing members or mounting zones requires prior structural approval, and works shall be supervised by client appointed supervisor to ensure compliance.

- APPENDIX A: ROOF AS-BUILT DRAWINGS AND RECOMMENDED MOUNTING REGIONS / FIXING MEMBERS

C

# FACILITY DESCRIPTION

Facility Name: Duayaw Nkwanta PEC

Facility Type: Building Structure

Location: Duayaw Nkwanta in the Ahafo Region (7°12′04.3″N, 2°06′44.5″W)

Duayaw Nkwanta PEC is a single-storey facility shared with other institutions. It is a masonry building with no recent structural upgrades. The PV system proposed is 6 kWp over 26.5 m² roof area.

- ROOF STRUCTURE AND FIELD OBSERVATION

The roof is a purlin-supported trussed system, pitched at 22°. It is constructed from timber, with trusses spaced at 2.1m centres. The trusses have members with typical cross-sectional dimensions of 100mm depth × 50mm width, while the purlins span 2.1m, spaced at 1050mm centres, with sections of 50mm depth × 100mm width. Pictorial representation of the as-built roof is shown in Figure 1.

Figure 7: Duayaw Nkwanta Roof Plan and Typical Section

Survey findings show that the trusses and purlins are in good condition, with no visible deterioration or structural distress. The spacing and member sizes are considered reasonable, and the roof performs as expected. The building overall appeared sound, with no structural issues of significance. Site photographs are presented in Figure 2.

Figure 8: Duayaw Nkwantai Site Pictures

- IDENTIFICATION OF MOUNTING AREAS AND FIXING MEMBERS

Purlins were found to be the most suitable fixing members, due to their closer spacing and easier access for mounting. Figure 3 shows the usable roof regions and proposed fixing members. The usable rooftop area available (46.0m2) is sufficient to accommodate the capacity of the proposed solar PV system.

Figure 9: Duayaw Nkwanta Suitable Spaces for the PV Installations

- VERIFICATION OF ROOF STRUCTURAL CAPACITY

The structural evaluation confirmed that all assessed roof members possess sufficient capacity to accommodate the demands from the proposed roof-top solar PV system. The combined effects of gravity and wind loads were found to be within acceptable limits. Accordingly, the roof can be considered structurally adequate for the safe installation of the proposed roof-top solar PV system, provided that anchoring and mounting are executed in line with the recommended fixing members and good engineering practice.

- TECHNICAL SPECIFICATION FOR MOUNTING

The following requirements ensure safe and structurally sound installation of the proposed roof-top PV system:

- Mount PV modules flush with the roof slope, maintaining a standoff < 300 mm, and place them within central roof zones identified in Appendix A (avoiding edges, corners, and overhangs).

- Fix rails directly to purlins, with rail spacing and anchor spacing each not exceeding 1.0 m, to ensure uniform distribution of PV and wind loads on purlins.

- Design anchorage for an unfactored uplift pressure of 1.0 kN/m².

- Use corrosion-resistant mounting components (galvanised steel, aluminium, or stainless steel), and isolate dissimilar metals to prevent galvanic corrosion.

- Seal all roof penetrations to maintain watertightness.

- Avoid stacking modules or concentrating installers at a single location to prevent temporary overloading of roof members.

- Any deviation from the specified fixing members or mounting zones requires prior structural approval, and works shall be supervised by client appointed supervisor to ensure compliance.

- APPENDIX A: ROOF AS-BUILT DRAWINGS AND RECOMMENDED MOUNTING REGIONS / FIXING MEMBERS

D

# FACILITY DESCRIPTION

Facility Name: Mampong PEC

Facility Type: Building Structure

Location: Mampong in the Ashanti Region (7o03I29.2IIN, 1o24I03.5IIW)

The Mampong PEC building is a masonry building with block walls providing support to the roof. It is an old single-storey construction which has not undergone any structural upgrade. The proposed PV system is 6 kWp covering 26.5 m² of roof area.

- ROOF STRUCTURE AND FIELD OBSERVATION

The roof is predominantly a gable (duopitch) roof with a 33.5° pitch. It has a couple-close (tied) rafter system made of timber material with rafters and ceiling joist serving as the primary components. Both rafters and ceiling joist have a 100mm depth x 50mm width cross sectional dimensions and are spaced at 950mm centres. The system spans 3.3 m, with walls serving as end supports. Purlins, which serve as secondary roof members, have sizes of 50mm depth x 100mm width and spacing of 900mm centres. Pictorial representation of the as-built roof is shown in Figure 1.

Figure 10: Mampong Roof Plan and Typical Section

The on-site survey revealed that the roof structure is in good physical condition with no visible deteriorations or distresses. The primary roof structure has reasonable spans, spacing and member sizes, typical of local practice. The building itself exhibited no visible cracks and any deformations of structural concern. Site photographs are presented in Figure 2.

Figure 11: Mampong Site Pictures

- IDENTIFICATION OF MOUNTING AREAS AND FIXING MEMBERS

Rafters were found to be the most suitable fixing members, owing to their stiffness, direct load path, shorter spacing, and ease of access. Figure 3 shows the usable roof regions and proposed fixing members. The usable rooftop area available (30.0m2) is sufficient to accommodate the capacity of the proposed solar PV system.

Figure 12: Mampong Suitable Spaces for the PV Installations

- VERIFICATION OF ROOF STRUCTURAL CAPACITY

The structural evaluation confirmed that all assessed roof members possess sufficient capacity to accommodate the demands from the proposed roof-top solar PV system. The combined effects of gravity and wind loads were found to be within acceptable limits. Accordingly, the roof can be considered structurally adequate for the safe installation of the proposed roof-top solar PV system, provided that anchoring and mounting are executed in line with the recommended fixing members and good engineering practice.

- TECHNICAL SPECIFICATION FOR MOUNTING

The following requirements ensure safe and structurally sound installation of the proposed roof-top PV system:

- Mount PV modules flush with the roof slope, maintaining a standoff < 300 mm, and place them within central roof zones identified in Appendix A (avoiding edges, corners, and overhangs).

- Fix rails directly to rafters, with rail spacing and anchor spacing each not exceeding 1.0 m, to ensure uniform distribution of PV and wind loads on rafters.

- Design anchorage for an unfactored uplift pressure of 1.0 kN/m².

- Use corrosion-resistant mounting components (galvanised steel, aluminium, or stainless steel), and isolate dissimilar metals to prevent galvanic corrosion.

- Seal all roof penetrations to maintain watertightness.

- Avoid stacking modules or concentrating installers at a single location to prevent temporary overloading of roof members.

- Any deviation from the specified fixing members or mounting zones requires prior structural approval, and works shall be supervised by client appointed supervisor to ensure compliance.

- APPENDIX A: ROOF AS-BUILT DRAWINGS AND RECOMMENDED MOUNTING REGIONS / FIXING MEMBERS

E

# FACILITY DESCRIPTION

Facility Name: Obuasi PEC

Facility Type: Building Structure

Location: Obuasi in the Ashanti Region (6°11′52.7″N, 1°39′43.9″W)

The Obuasi PEC building is a masonry structure with block walls supporting the roof. It is an old single-storey facility with no known renovations or structural upgrades. The PV system proposed is 6 kWp over 26.5 m² roof area.

# ROOF STRUCTURE AND FIELD OBSERVATION

The roof is a monopitch roof with a low slope of about 10°. It is framed with a rafter system constructed from timber. The rafters, which form the primary roof members, have cross-sectional dimensions of 150mm depth × 50mm width and are spaced at 1200mm centres. They span a projected length of 4.62m, supported at their ends by the masonry walls. Purlins with size of 75mm depth × 50mm width and spacing of 1100mm serve as secondary members, providing intermediate support to the roof covering. Pictorial representation of the as-built roof is shown in Figure 1.

Figure 13: Obuasi Roof Plan and Typical Section

The on-site inspection showed that the rafters and purlins are in good condition, with no visible deterioration or signs of distress. The spans, spacing, and sizes of members are considered reasonable and typical of local construction practice. The building appeared structurally robust, with no visible cracks, deformations, or distress of concern. Site photographs are presented in Figure 2.

Figure 14: Obuasi Site Pictures

# IDENTIFICATION OF MOUNTING AREAS AND FIXING MEMBERS

Rafters were found to be the most suitable fixing members, owing to their stiffness, direct load path, shorter spacing, and ease of access. Figure 3 shows the usable roof regions and proposed fixing members. The usable rooftop area available (48.0m2) is sufficient to accommodate the capacity of the proposed solar PV system.

Figure 15: Obuasi Suitable Spaces for the PV Installations

# VERIFICATION OF ROOF STRUCTURAL CAPACITY

The structural evaluation confirmed that all assessed roof members possess sufficient capacity to accommodate the demands from the proposed roof-top solar PV system. The combined effects of gravity and wind loads were found to be within acceptable limits. Accordingly, the roof can be considered structurally adequate for the safe installation of the proposed roof-top solar PV system, provided that anchoring and mounting are executed in line with the recommended fixing members and good engineering practice.

# TECHNICAL SPECIFICATION FOR MOUNTING

The following requirements ensure safe and structurally sound installation of the proposed roof-top PV system:

- Mount PV modules flush with the roof slope, maintaining a standoff < 300 mm, and place them within central roof zones identified in Appendix A (avoiding edges, corners, and overhangs).

- Fix rails directly to rafters, with rail spacing and anchor spacing each not exceeding 1.0 m, to ensure uniform distribution of PV and wind loads on rafters.

- Design anchorage for an unfactored uplift pressure of 1.0 kN/m².

- Use corrosion-resistant mounting components (galvanised steel, aluminium, or stainless steel), and isolate dissimilar metals to prevent galvanic corrosion.

- Seal all roof penetrations to maintain watertightness.

- Avoid stacking modules or concentrating installers at a single location to prevent temporary overloading of roof members.

- Any deviation from the specified fixing members or mounting zones requires prior structural approval, and works shall be supervised by client appointed supervisor to ensure compliance.

# APPENDIX A: ROOF AS-BUILT DRAWINGS AND RECOMMENDED MOUNTING REGIONS / FIXING MEMBERS

F

# FACILITY DESCRIPTION

Facility Name: Offinso PEC

Facility Type: Building Structure

Location: Offinso in the Ashanti Region (6°56′31″N, 1°40′27.5″W)

The Offinso PEC is housed within the ground floor of a multi-storey building that is still under construction, currently at the first-floor slab level. It is a shared facility with other institutions. The proposed PV system is 6 kWp over 26.5 m² roof area.

# ROOF STRUCTURE AND FIELD OBSERVATION

The first floor slab temporarily serves as the roof over the ground floor. The slab is part of a reinforced concrete beam-slab floor system, with a thickness of 150mm. The beams and slab spans are typical of conventional reinforced concrete construction, with reinforced concrete columns and block walls providing support below. Pictorial representation of the as-built roof is shown in Figure 1.

Figure 16: Offinso Roof Plan and Typical Section

Inspection revealed the slab to be robust, with no cracks or deflections of structural concern. As construction progresses, the slab will eventually serve as an intermediate floor, but at present, it adequately functions as the roof without signs of distress. Site photographs are presented in Figure 2.

Figure 17: Offinso Site Pictures

# IDENTIFICATION OF MOUNTING AREAS AND FIXING MEMBERS

The reinforced concrete floor slab serves as the fixing member and offers locations along its surface for anchorage. Figure 3 shows the usable roof region of 155.0m2, which is sufficient to accommodate the capacity of the proposed solar PV system.

Figure 18: Offinso Suitable Spaces for the PV Installations

# VERIFICATION OF ROOF STRUCTURAL CAPACITY

The available reinforced concrete first-floor slab, which serves as the roof surface, was visually assessed to be robust and capable of supporting the proposed PV installation without the need for further analysis.

# TECHNICAL SPECIFICATION FOR MOUNTING

The following requirements apply to the installation of the PV modules on the flat concrete roof:

- Use ballasted systems or approved mechanical fixing methods; all penetrations shall be fully sealed to maintain watertightness.

- Anchorage or ballast shall resist an unfactored uplift pressure of 1.0 kN/m², with anchor capacity and ballast weight sized accordingly.

- Modules shall be installed only in central roof zones (see Appendix A), avoiding edges and corners.

- All mounting components shall be corrosion-resistant (galvanised steel, aluminium, or stainless steel), with dissimilar metals isolated to prevent galvanic corrosion.

- Any deviation from the specified fixing members or mounting zones requires prior structural approval, and works shall be supervised by client appointed supervisor to ensure compliance.

# APPENDIX A: ROOF AS-BUILT DRAWINGS AND RECOMMENDED MOUNTING REGIONS / FIXING MEMBERS

G

# FACILITY DESCRIPTION

Facility Name: Sunyani PEC

Facility Type: Building Structure

Location: Sunyani in the Bono Region (7°20′23.1″N, 2°20′06.6″W)

The Sunyani PEC building is a masonry building with block walls supporting the roof. It is an old single-storey construction which has not undergone any structural upgrade. The proposed PV system is 6 kWp over 26.5 m² roof area.

# ROOF STRUCTURE AND FIELD OBSERVATION

The roof structure is a couple-close (tied) rafter system made of timber. The rafters are spaced at 820mm centres, each with cross-sectional dimensions of 100mm depth × 50mm width. The ceiling joists, which act as ties, span 4.2m with similar sectional dimensions and spacing. Purlins with size of 50mm depth x 100mm width and spacing of 1100mm centres provide intermediate support for the roof covering. Pictorial representation of the as-built roof is shown in Figure 1.

Figure 19: Sunyani Roof Plan and Typical Section

Inspection revealed the roof structure to be in good physical condition, with no signs of distress or material deterioration. The spans, spacing, and member sizes are reasonable and in line with local construction norms. The building is robust, with no observed structural defects. Site photographs are presented in Figure 2.

Figure 20: Sunyani Site Pictures

# IDENTIFICATION OF MOUNTING AREAS AND FIXING MEMBERS

Rafters were found to be the most suitable fixing members, owing to their stiffness, direct load path, shorter spacing, and ease of access. Figure 3 shows the usable roof regions and proposed fixing members. The usable rooftop area available (50.0m2) is sufficient to accommodate the capacity of the proposed solar PV system.

Figure 21: Sunyani Suitable Spaces for the PV Installations

# VERIFICATION OF ROOF STRUCTURAL CAPACITY

The structural evaluation confirmed that all assessed roof members possess sufficient capacity to accommodate the demands from the proposed roof-top solar PV system. The combined effects of gravity and wind loads were found to be within acceptable limits. Accordingly, the roof can be considered structurally adequate for the safe installation of the proposed roof-top solar PV system, provided that anchoring and mounting are executed in line with the recommended fixing members and good engineering practice.

# TECHNICAL SPECIFICATION FOR MOUNTING

The following requirements ensure safe and structurally sound installation of the proposed roof-top PV system:

- Mount PV modules flush with the roof slope, maintaining a standoff < 300 mm, and place them within central roof zones identified in Appendix A (avoiding edges, corners, and overhangs).

- Fix rails directly to rafters, with rail spacing and anchor spacing each not exceeding 1.0 m, to ensure uniform distribution of PV and wind loads on rafters.

- Design anchorage for an unfactored uplift pressure of 1.0 kN/m².

- Use corrosion-resistant mounting components (galvanised steel, aluminium, or stainless steel), and isolate dissimilar metals to prevent galvanic corrosion.

- Seal all roof penetrations to maintain watertightness.

- Avoid stacking modules or concentrating installers at a single location to prevent temporary overloading of roof members.

- Any deviation from the specified fixing members or mounting zones requires prior structural approval, and works shall be supervised by client appointed supervisor to ensure compliance.

# APPENDIX A: ROOF AS-BUILT DRAWINGS AND RECOMMENDED MOUNTING REGIONS / FIXING MEMBERS

H

# FACILITY DESCRIPTION

Facility Name: Tema PEC

Facility Type: Building Structure

Location: Tema in the Greater Accra Region (5°38′21.9″N, 0°00′21.1″W)

Tema PEC facility is a single-storey reinforced concrete portal frame structure, with the portal frames forming both the primary building system and the primary roof structure. It is an old construction, and has not undergone any structural upgrade.  The PV system proposed is 30 kWp over 138 m² roof area.

# ROOF STRUCTURE AND FIELD OBSERVATION

The roof is a purlin-supported system, pitched at about 24°. The RC portal frames are rigid and robust, spaced at 4.9m centres, and serve as the integral loadbearing system of the building. Timber purlins, measuring 150mm depth × 50mm width, span between the portal frames at 850mm centres, providing intermediate support to the roof covering. Pictorial representation of the as-built roof is shown in Figure 1.

Figure 22: Tema Roof Plan and Typical Section

The field survey confirmed that the building and roof structure are in excellent physical condition. The integration of the RC portal frames into both the building and roof system ensures high robustness and stability. The purlins have reasonable spans and spacing, and all components appeared sound with no visible defects. Overall, the Tema PEC building is structurally very robust, with no evidence of distress or deterioration of significance. Site photographs are presented in Figure 2.

Figure 23: Tema Site Pictures

# IDENTIFICATION OF MOUNTING AREAS AND FIXING MEMBERS

Purlins were found to be the most suitable fixing members, due to their closer spacing and easier access for mounting. Figure 3 shows the usable roof regions and proposed fixing members. The usable rooftop area available (140.0m2) is sufficient to accommodate the capacity of the proposed solar PV system.

Figure 24: Tema Suitable Spaces for the PV Installations

# VERIFICATION OF ROOF STRUCTURAL CAPACITY

The structural evaluation confirmed that all assessed roof members possess sufficient capacity to accommodate the demands from the proposed roof-top solar PV system. The combined effects of gravity and wind loads were found to be within acceptable limits. Accordingly, the roof can be considered structurally adequate for the safe installation of the proposed roof-top solar PV system, provided that anchoring and mounting are executed in line with the recommended fixing members and good engineering practice.

# TECHNICAL SPECIFICATION FOR MOUNTING

The following requirements ensure safe and structurally sound installation of the proposed roof-top PV system:

- Mount PV modules flush with the roof slope, maintaining a standoff < 300 mm, and place them within central roof zones identified in Appendix A (avoiding edges, corners, and overhangs).

- Fix rails directly to purlins, with rail spacing and anchor spacing each not exceeding 1.0 m, to ensure uniform distribution of PV and wind loads on purlins.

- Design anchorage for an unfactored uplift pressure of 1.0 kN/m².

- Use corrosion-resistant mounting components (galvanised steel, aluminium, or stainless steel), and isolate dissimilar metals to prevent galvanic corrosion.

- Seal all roof penetrations to maintain watertightness.

- Avoid stacking modules or concentrating installers at a single location to prevent temporary overloading of roof members.

- Any deviation from the specified fixing members or mounting zones requires prior structural approval, and works shall be supervised by client appointed supervisor to ensure compliance.

# APPENDIX A: ROOF AS-BUILT DRAWINGS AND RECOMMENDED MOUNTING REGIONS / FIXING MEMBERS