## Specification
Position | Item | Description | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns A-C, please indicate "Yes". Otherwise, describe your special features in this column. | Quantity / Capacity | Unit
1 | General Requirements
1.1 | PV Plant | see spread sheet "Sites" |  |  | kWp
1.2 | Site description | see spread sheet "Sites"
1.3 | Power grid | The PV systems are to be hybrid system - to balance the benefits of solar generation with grid electricity. The specifications of the grid operators are to be completely fulfilled technically especially the need to limit export to the grid for buildings without net-meters. The PV systems shall meet applicable Ghana Building Code and National Electricity Distribution Code requirements as well as other prudent best practices.
1.4 | Preliminary design principles | The contractor shall propose a solar plant with battery design and integration drawings that meet the nominal least capacity specified for each of the selected site (as referenced in the spread sheet "Sites"). The bidder shall propose the expected annual energy generation, as well as the expected energy generation per month, for each site. Additionally, the bidder must provide references for the database and software used for the design. The drawings and schematic layouts must indicate the proposed location of the panel array(s); access points along with a one-line electrical diagram showing inverters, combiner box, meters, and points of common coupling could be identified. All components offered must comply with below technical requirements and fully functional and compatible with each other. All components and parts that are not explicitly mentioned in this document, but are necessary to ensure a faultless layout, installation and professional operation must be offered by the bidder (except for parts that are explicitly excluded from the tender).
2 | Photovolatic Modules
2.1 | Photovolatic Modules | The module shall meet the following technical requirements, minimum standards and specifications: - the minimum technical specifications of the proposed nominal capacities [see spread sheet "Sites"] - 60 or 72 cell PV modules with crystalline technology - Output per module min. 280 Wp (60 cells) / 330 Wp (72 cells), tolerance 0 - 5%. - Certification for wind load up to minimum 2400 Pa - Solar cells shall be embedded in an EVA (ethylene vinyl acetate) layer, anti-reflective coating, front cover made of specially tempered, highly transparent glass. Framed with aluminium profile (anodised). - Maximum NOCT 45±2°C. The PV modules shall be capable of operating under extreme temperature (up to +50°C) and humidity (up to 95%) conditions. |  |  | No.
2.2 | Certifications and standards | The module complies with the following standards and certifications: - IEC 61 215 : Terrestrial photovoltaic (PV) modules - Type qualification and type approval. - IEC 61 730 : Photovoltaic (PV) modules - safety qualification The tests are carried out by recognised testing laboratories according to ISO/IEC 17025. The manufacturer of the solar modules can prove by a suitable certificate that a permanent quality control and assurance of the production processes takes place in his factory. It must be proven that the standards according to IEC 61215 and IEC 61730 are also adhered to in ongoing production. The certificate itself is issued by an accredited testing institute. The normative requirements IEC 60891 ; IEC 60904 ; IEC 61345 ; IEC 61701; IEC 61721; EN 50380 are fulfilled. CE Declaration of Conformity by the manufacturer is available. A confirmation by a conformity assessment body according to ISO/IEC 17021 is available. CE marking of the solar modules is available. The solar modules are marked accordingly. Weatherproof junction box on the back of the module. The junction box must comply with at least IP 65 and the DIN VDE 0126-5 standard. The cabling between the modules with connectors complies with the EN 50521 standard.
2.3 | Delivery | All items delivered will be inspected, confirmed and approved by our GIZ technical team that it meets specification before payment made to supplier. The modules must be packed in wooden boxes or equivalent. IEC 62759-1 shall be observed with regard to the delivery/shipping of the modules. Flash data for each module must be provided as a digital file.
2.3 | Warranty | Linear performance guarantee for 25 years with maximum degradation coefficient of -0.5%/year Product guarantee for at least 10 years If the rated power of the modules is undershot within the guaranteed warranty period, the modules will be replaced free of charge at the installation site. |  |  | yrs
2.4 | Please specify: | Brand name, model, type
|  | Area of the cells (LxW) in mm |  |  | mm
|  | Dimensions of the module (LxWxD) in mm |  |  | mm
|  | Weight of module in kg |  |  | kg
|  | Maximum power (Pmax) W |  |  | W
|  | Maximum voltage ( Vmax) V |  |  | V
|  | Maximum current ( Ipmax) A |  |  | A
|  | Maximum reverse current IR [A] |  |  | A
|  | Short-circuit current (Isc) A |  |  | A
|  | Open circuit voltage ( Voc) V |  |  | V
|  | Temperature coefficient for current A/°C |  |  | A/°C
|  | Temperature coefficient for voltage V/°C |  |  | V/°C
|  | Temperature coefficient for power %/°C |  |  | %/°C
|  | Nominal cell operating temperature ( NOCT) |  |  | NOCT
|  | Maximum system voltage ( Vsmax ) |  |  | Vsmax
|  | Operating temperature ( Min- Max ) °C |  |  | °C
|  | Ambient temperature ( Min - Max ) °C |  |  | °C
Current-voltage characteristics at 25°C and other temperatures and irradiation
2.5 | Please enclose with quotation: | Data sheet
Test certificates according to IEC 61215 and IEC 61730
Certificates according to ISO/IEC 17025
Accreditation of the test centre/institute or test centres (IEC 61215, IEC 61730 and ISO/IEC 17025) according to EN 45011 - 45013
CE declaration of conformity of the manufacturer
Confirmation that upon delivery of the modules, the flasher protocols showing the rated power of all delivered modules are presented and handed over.
Declaration or explicit confirmation regarding the replacement of the modules according to item 2.3.
Explanations on packaging and handling of the solar modules with reference to IEC 62759-1
2.6 | EL measurements | The results and images of the flash tests and electroluminescence measurements issued to the serial numbers of the panels shall be submitted. All documents and technical documentation submitted must be legible and easily recognisable.
3 | Structure
3.1 | Structure | see spread sheet "Sites"
3.2 | Roof conditions / description | see Annex 2 More detailed information and drawings for the construction sites are available and will be provided on request and confidentiality declaration.
3.3 | Requirement | Compliant with Ghana Fire Service code and ordinance requirements for roof access; and all applicable Ghana Building Code and local assembly codes and standards. Structure design shall address access for maintenance and replacement of the equipment. All structural components shall be non-corrosive (galvanized steel, stainless steel or aluminium).
3.4 | Warranty | min. 10 years |  |  | yrs
3.5 | Please specify: | Brand name, model, type
Data sheet
Detailed description of the anti-theft screws and nuts
Technical description of the substructure (angle of tilt, etc)
Anti-theft bolts and nuts to match the modules
Description of the lightning protection and earthing
3.6 | In case of order, to be provided before delivery: | Sectional drawings of the profiles and elevations
Detailed drawings of fixings (interfaces, connections)
Assembly instructions in English
4 | Inverter
4.1 | Hybrid Inverter | The hybrid inverter shall meet the following requirements, minimum standards and specifications: - meets the minimum technical requirements of the Electricity Company of Ghana as well as the technical specification of the current National Electricity Distribution Code. - Compatible with supplied storage batteries - Forced air or natural convection cooling method - Wall-mounted or floor-standing - In-built charge controller (MPPT) - Enables supply of consumers with 230 V AC - Simultaneously allows connection to a battery bank or power grid - Capable of integrating a battery storage and caharging a battery bank - Continuous power (capacity must be sufficient according to the PV-plants capacity) - System voltage 48 V - Output voltage 230 V AC +/- 5% - Output frequency 50/60 Hz - Pure sine wave voltage - Integrated MPP tracker, multi-stage charging technology - Adjustable end-of-charge voltages - Adjusted to the interconnecting solar modules from positions - Input voltage 90 - 280 V AC - Input frequency 40 - 65 Hz; Automatic recognition 50/60 Hz - Max.current on transfer system 120 A - Efficiency >90% - Harmonic distortiion <3% |  |  | No.
4.2 | Handling | Monitoring features including visual operation indicators by LED/ Display; electronic data storage facility on SD/MMC card and/or state-of-the art data communication ports. Menu-guided operation Serial interface RS-232, PC connection via USB Incl. PC software
4.3 | Power protection | Voltage and Frequency Protection Islanding Protection and Anti-Islanding Detection Overvoltage and Under-Voltage protection Current Limiting and Short Circuit Protection Anti-Reverse Protection Ground Fault Protection Temperature and load protection Surge and Lightning Protection Battery overcharge/over-discharge protection
4.4 | Certifications and standards | It must comply with the following standards: EN-IEC 60335-1, EN-IEC 60335-2-29, EN-IEC 62109-1, EN 55014-1, EN 55014-2, EN-IEC 61000-3-2, IEC 61000-6-1, IEC 61000-6-2, IEC 61000-6-3. Manufactured according to ISO 9001 and ISO 14001. CE compliant
4.5 | Warranty | min. 5 years |  |  | yrs
4.6 | Please specify: | Brand name, model, type
Waveform
|  | Dimension (LxWxD) in mm |  |  | mm
|  | Weight of module in kg |  |  | kg
|  | Maximum power (W) |  |  | W
|  | Nominal Ccontinuous power (W) |  |  | W
|  | Input Current (A) |  |  | A
|  | Nominal input voltage (VDC) |  |  | VDC
|  | Input voltage range (VDC) |  |  | VDC
|  | Nominal output voltage (VAC) |  |  | VAC
|  | Number of MPPT Trackers |  |  | No.
|  | AC voltage range (%) |  |  | %
|  | Voltage regulation (%) |  |  | %
|  | AC power frequency (Hz) |  |  | Hz
|  | Maximum ambient temperature (°C) |  |  | °C
|  | Max Charging Current (A) |  |  | A
Communication/interfaces: RS485, USB, Ethernet
|  | Efficiency (%) |  |  | %
Transformerless inverter protection class (IP)
MPPT Operating Voltage Range
Integrated data logger
|  | Permissible humidity (%) |  |  | %
IP Rating (indoor & outdoor)
Data sheet
5 | Battery
5.1 | Lithium-ion-battery | 3,000 cycles @50% DoD, 20°C / 1,500 cycles @80% DoD, 20°C [for smaller only 2,500 @50 DoD 20°C] Proof of conformity and performance: IEC 60896-21/22 and IEC 61427-2 is required. Service life according to EUROBAT min. 12 years at 20°C Standards and regulations for installation: DIN EN 50272-2 (safety regulations for battery rooms) The battery must be supplied with its rack certified by the manufacturer. Proof of quality assurance system according to ISO 9001 / ISO 14001 ISO 45001;IEC 62619, UL 1973 occupational health and safety or equivalent certification Integration with hybrid inverters and monitoring apps Fully insulated, corrosion-free lead terminal All pole penetrations must ensure complete electrolyte and gas tightness even when positive plate is growing Fully insulated copper connectors and screw heads Interconnection lead poles with torque 20 - 22 Nm Environmentally friendly, min. 98 % recyclable Energy efficiency > 80% Ampere-hour efficiency > 90% Self-discharge less than 2-3%/month at 20°C No memory effect Sufficiently large containers for electrolyte circulation Each battery is labelled with at least the following data: Manufacturer, type, model number, nominal voltage in V, nominal capacity in Ah, month and year of commissioning. Each cell must have a factory serial number |  |  | No.
5.2 | Battery Management System (BMS) / Protection | Protection functions: Short-circuit proof Cell balancing Overload protection Deep discharge Overcharging Overtemperature protection Lightning and overvoltage protection AC side Compliance with other VDE/IEC regulations (contact protection etc.) Compliance with EMC limits (electromagnetic compatibility) according to EN 50081 and EN 55014 Radio interference suppression (VHF) Output power control of the feed-in inverter (item 1.3) via frequency for overcharge protection of the battery Other normative requirements IEC 62093 ;DIN EN 5178 ; are fulfilled CE declaration of conformity by the manufacturer is available. Confirmation by a conformity assessment body in accordance with ISO/IEC 17021 is available. CE marking of the battery-charging inverter is available. The battery charging inverters are marked accordingly. Communication point Control cable (e.g. LIYCY paired 2x2x0.25 or comparable type) if necessary
5.3 | Please specify: | Brand name, model, type
|  | Nominal Voltage |  |  | V
|  | Nominal Capacity |  |  | Ah
|  | Energy Capacity |  |  | kWh
|  | Weight of module |  |  | kg
|  | Voltage Range per cell |  |  | V
|  | Depth of Discharge (DoD) |  |  | %
|  | Cycle Life (@50% or 80% DoD) |  |  | A
IP Rating (indoor & outdoor)
Data sheet
5.4 | Warranty | min. 5 years |  |  | yrs
6 | Monitoring and Verification (M&V) Components
| Monitoring and Verification (M&V) | The bidder shall provide the following M&V services: - Provide a design / layout, technical hardware and software solution to monitor, record, store and/or transmit the energy performance data of the solar plant and batteries as well as the building in a time granularity of at least 15 minutes concerning the total energy output, export of power and import of power by the buildings - Provide complete documentation of the technical details of the M&V system - Provide user manuals and training for operating the M&V system - Install and commission M&V equipment. - Provide services for a period of 12 months to operate the M&V system after commissioning of the SPV - Cloud based recording is a requirement
7 | Cable, Combiner Box, Connectors and Distribution Panel
7.1 | Requirement | The wiring, combining box, connectors and distribution panel(s) shall meet the following requirements, minimum standards and specifications: - Areas where wiring passes through ceilings, walls or other areas of the building shall be properly restored, booted, sealed and returned to their original condition. Fire protection regulations have to be kept; fire shutters have to be installed were necessary. - All wiring between combiner box, distribution panel and the point of interconnection shall be invisible and meet applicable codes. - All outdoor electrical devices shall have the capability to be locked as appropriate. - Wiring and connections shall fulfil these standards and conditions; TUV PfG 1169/08.2007, EN 50396, IEC/EN 60332-1-2, HD 605/A1, EN 50267-2-1, EN 60684-2, IEC /EN 60811-2-1, EN 50267-2-2, HD 605/A1, EN 50521 and Direct Current wiring loss-es max. 1.5%. - Distribution panel, combiner box and lighting protection shall fulfil these standards and conditions (where applicable); IEC 60364, KS 04-192: 1988, KS 04 -194: 1990, KS 04 -187/188, KS 04 -290: 1987, IEC 62305, KS 04-179: 1983; UV and water-resistant material, MCB / MCCB outdoor cabinets and enclosures, SPDs class II - IEC 61643-11 and operating temperature up to 80°C, non-metallic fiberglass enclosures with clear polycarbonate covers
7.2 | Cables | 1x [4, 6 or 10] mm² copper cable with double insulation for up to 1000V, type C2 (high flame resistance), AN3 (high UV resistance) Maximum permissible conductor temperature at least 90°C in continuous use. The standard EN 50618 is fulfilled.
7.3 | Empty conduits | PE cable conduits for burial, double wall (corrugated outside, smooth inside according to standard NF EN 50086-2-4)
7.4 | Cable ties | UV-resistant cable ties in all necessary sizes and quantities.
7.5 | Accessories | All accessories for proper fastening of the cables under the modules for the entire installation.
7.6 | AC or DC combiner box | Provide IP65-rated AC/DC combiner box(es) complete with appropriately rated isolators, circuit protection, and surge protection devices (SPD).
7.7 | Switch cabinet | Provide a lockable switch cabinet/distribution board housing all required switching, protection, isolation, and metering equipment, adequately rated for the system capacity.
7.8 | Earthing system | Provide a complete earthing and bonding system for all PV and electrical equipment, achieving an earth resistance of ≤ 5 Ω or as required by applicable standards
8 | Documentation
| The following documentation, manuals and software in English, must be supplied in electronic form for all components of the system after the order has been placed: | For documentation, IEC 62446-1:2016 standard shall be fulfilled by contractor. Assembly instructions for the entire system. Overview for an installer on site, showing which components are connected to each other and how. This overview also refers to the corresponding installation instructions and assembly instructions for the individual components.
Overview of proposed solar PV plant and performance characteristics
Circuit documentations
Description of the components
Wiring diagrams, layouts, scheme of switches and combiner boxes
Assembly instructions, installation instructions
Commissioning instructions
Operating & maintenance instructions / manual
Manual, Data sheets and Maintenance instructions
Error analysis and troubleshooting suggestions in the event of a malfunction
ALL Warrantees
9 | Material Delivery FCA Hamburg Seaport
All material must be shipped FCA Hamburg Seaport (after Waybill, packing list and invoice has been shared and GIZ has confirmed receipt of tax exemption). Delivery should not be latest 2 months after order.
| Please specify: | Dimensions (LxWxH), weight (kg) incl. packaging for sea shipment.
9a | Material Delivery CIF Tema (Accra) Seaport (optional)
All material must be delivered at CIF Tema (Accra) Seaport latest 2 months. This option can also be offered as an alternative to transport to FCA Hamburg Seaport. FCA Hamburg Seaport must be offered, as this forms the basis of the evaluation.
9b | Customs clearance (by giz)
Customs clearance will be done by GIZ Ghana (Consignee). Detailled address will follow after the order.
9c | Domestic Material Transport to storage place (by giz)
| Domestic Material Transport to storage place (by giz) | Domestic transport will be done by giz to supplier's, or agent's warehouse in Accra. Bidder has to organize and provide a safe storage place close to Accra. Please calculate 5 days after customs clearance for transport from Accra customs to supplier's storage at Accra by giz.
9d | Domestic Material Transport on each site
| Domestic Material Transport | Bidder has to organize and provide a safe storage place close to Accra. All transports to each site are in the scope and responsibilty of the bidder.
10 | Service on site
| Please enclose with the offer: | Installation roadmap for each site for approval by the GIZ technical team
The bidder must have all required licenses and accreditation to install solar plant in Ghana. The bidder must prove that only authorised companies and qualified / experienced experts from Ghana may undertake the installation and commissioning on site.
Installation and commissioning of all components of the complete solar PV plant at each site. The supplier shall be responsible for carrying out of all related electrical works and supplying of all necessary electrical equipment for the proper operation of the supplied technological equipment. Installation and commissioning at each site must be conducted according to Ghana electrical quality and safety norms and standards. At least two (2) certified solar technician from Ghana should be in the team to perfom the solar installation and commissioning. Complete inspection, testing and commissioning of the solar PV plant incl. function tests and trial operation in cooperation with GIZ technical team / Consultant. The technical commissioning of the solar plant will include training on the operation of the solar PV plant and its components.
Accessory Material for required adaptations (installation) will specified in type and quantities after contract conclusion and final solar PV plant design. Necessary planning and preparation work before installation at each site have to be considered and taken care of by the Contractor. The project, including supports and power conductors, shall not interfere with roof drains, water drainage, expansion joints, air intakes, existing electrical and mechanical equipment, existing antennas, and planned areas for future installation of equipment shown on existing drawings. Please describe which preparation work should be provided. All installations and equipment will be inspected and their functionality will be tested. It will be visually checked for compliance with the final design, technical specifications and approved quotation. The completeness of drawings, operation and maintenance manuals will be checked as well. Furthermore it will be verified that the installation personnel at each site are adequately trained and have the required qualifications. A test will be carried out to demonstrate that the solar PV plant can be operated according to the technical specifications under all available operating conditions. To allow also a remote inspection by a Consultant, fotos and videos of the installation and the equipment have to be taken and send to GIZ for verification.
Documentation: All work steps will be documented in detail throughout the installation phase. The documentation will include the final (actual) wiring diagram of all components and the solar PV plant. The contractor shall deliver a completion report containing “as-built drawings" and all other project documents based upon actual site installation. The contractor shall submit six (6) hard copies and two (2) pen drives containing the “as-built” drawings/designs and specifications as CAD and PDF files.
Indication of what kind of service can be provided (spare parts procurement, spare parts exchange, fault analysis with repair etc.) Contractor shall be responsible for the security of all components on site untill handover All defects shall be corrected before final payment. Final payment will be issued against acceptance certificate for each site issued by GIZ team and Consultant
11 | Warranty
| min. 2 years | On the entire system and installation. Fully according to GIZ General Purchase Conditions 2023. This warranty takes precedence over product and manufacturer warranties. For individual components, longer warranty periods apply if described.
| Guarantee assignment declarations | All warranties must be assigned to GIZ and project partners by declaration. This declaration must be signed and stamped by each manufacturer.
12 | Training
| Present Training | The Contractor shall provide a 1–2-day onsite practical training in English for ten (10) participants comprising one (1) representative from each of the eight (8) beneficiary offices and two (2) representatives from the Labour Department Headquarters. The training shall cover system operation, performance monitoring, troubleshooting, basic maintenance, and maintenance contract management for the solar PV system and associated equipment. The Contractor shall be responsible for all training logistics, including training materials, PPE, tools, venue arrangements (where required), and catering/refreshments. Attendance records and training materials shall be provided upon completion of the training.
13 | Maintenance
| 1 year after commissioning | 1 regular maintenance per year

## Sites
No | Region | Site name | Minimum Requirements PV Plants | Site Description | Structure
1 | Bono Region | Wenchi Labour Office / PEC | Nominal solar plant capacity at least 6 kWp Nominal battery capacity at least 12 kWh - Rooftop mounted solar PV system - With back-up storage batteries - Hybrid solar PV system | The plant is to be erected in Wenchi, Bono Region. GPS Location: 7°44′38.6″N, 2°06′01.8″W Building picture: refer to Annex 2 | The substructure made of aluminium or steel must support the modules and withstand the local weather conditions. It must be sufficiently protected against corrosion. Roof type: Monopitch Rafter Roof Roof picture: refer to Annex 2
2 | Bono Region | Sunyani Labour Office / PEC | Nominal solar plant capacity at least 6 kWp Nominal battery capacity at least 12 kWh - Rooftop mounted solar PV system - With back-up storage batteries - Hybrid solar PV system | The plant is to be erected in Sunyani, Bono Region. GPS Location: 7°20′23.1″N, 2°20′06.6″W Building picture: refer to Annex 2 | The substructure made of aluminium or steel must support the modules and withstand the local weather conditions. It must be sufficiently protected against corrosion. Roof type: Tied Rafter Roof Roof picture: refer to Annex 2
3 | Ahafo Region | Duayaw Nkwanta Labour Office / PEC | Nominal solar plant capacity at least 6 kWp Nominal battery capacity at least 12 kWh - Rooftop mounted solar PV system - With back-up storage batteries - Hybrid solar PV system | The plant is to be erected in Duayaw Nkwanta, Ahafo Region. GPS Location: 7°12′04.3″N, 2°06′44.5″W Building picture: refer to Annex 2 | The substructure made of aluminium or steel must support the modules and withstand the local weather conditions. It must be sufficiently protected against corrosion. Roof type: Purlin-Supported Trussed Roof Roof picture: refer to Annex 2
4 | Ashanti Region A | Mampong Labour Office / PEC | Nominal solar plant capacity at least 6 kWp Nominal battery capacity at least 12 kWh - Rooftop mounted solar PV system - With back-up storage batteries - Hybrid solar PV system | The plant is to be erected in Mampong, Ashanti Region. GPS Location: 7°03'29.2"N, 1°24'03.5"W Building picture: refer to Annex 2 | The substructure made of aluminium or steel must support the modules and withstand the local weather conditions. It must be sufficiently protected against corrosion. Roof type: Tied Rafter Roof Roof picture: refer to Annex 2
5 | Ashanti Region A | Offinso Labour Office / PEC | Nominal solar plant capacity at least 6 kWp Nominal battery capacity at least 12 kWh - Rooftop mounted solar PV system - With back-up storage batteries - Hybrid solar PV system | The plant is to be erected in Offinso, Ashanti Region. GPS Location: 6°56′31″N, 1°40′27.5″W Building picture: refer to Annex 2 | The substructure made of concrete must support the modules and withstand the local weather conditions. It must be sufficiently protected against corrosion. Roof type: RC Floor Slab Roof picture: refer to Annex 2
6 | Ashanti Region B | Obuasi Labour Office / PEC | Nominal solar plant capacity at least 6 kWp Nominal battery capacity at least 12 kWh - Rooftop mounted solar PV system - With back-up storage batteries - Hybrid solar PV system | The plant is to be erected in Obuasi, Ashanti Region. GPS Location: 6°11′52.7″N, 1°39′43.9″W Building picture: refer to Annex 2 | The substructure made of aluminium or steel must support the modules and withstand the local weather conditions. It must be sufficiently protected against corrosion. Roof type: Monopitch Rafter Roof Roof picture: refer to Annex 2
7 | Ashanti Region B | Bekwai Labour Office / PEC | Nominal solar plant capacity at least 6 kWp Nominal battery capacity at least 12 kWh - Rooftop mounted solar PV system - With back-up storage batteries - Hybrid solar PV system | The plant is to be erected in Bekwai, Ashanti Region. GPS Location: 6°27′21.3″N, 1°34′55.5″W Building picture: refer to Annex 2 | The substructure made of aluminium or steel must support the modules and withstand the local weather conditions. It must be sufficiently protected against corrosion. Roof type: Strutted Ridge-Supported Rafter Roof Roof picture: refer to Annex 2
8 | Greater Accra Region | Tema Labour Office / PEC | Nominal solar plant capacity at least 30 kWp Nominal battery capacity at least 60 kWh - Rooftop mounted solar PV system - With back-up storage batteries - Hybrid solar PV system | The plant is to be erected in Tema, Greater Accra Region. GPS Location: 5°38′21.9″N, 0°00′21.1″W Building picture: refer to Annex 2 | The substructure made of aluminium or steel must support the modules and withstand the local weather conditions. It must be sufficiently protected against corrosion. Roof type: Portal Frame with Purlin-Supported Roof Roof picture: refer to Annex 2