## Specification
Position | Item | Description | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns A-C, please indicate "Yes". Otherwise, describe your special features in this column.
1 | General Requirements
1.1 | PV Plant | System size at least min. 38,4 kWp reasonable number of modules to achieve requested system size - Flatrooftop system - Battery storage - Grid connection
1.2 | Site conditions | All plants are to be erected in Ukraine and must fit to Ukrainian weather conditions. All components must be designed accordingly!
1.3 | Power grid | The PV systems are to be fully connected to the local electricity grid. The specifications of the grid operators are to be completely fulfilled technically.
1.4 | Basic design principles | The components offered must be fully functional and compatible with each other. All components and parts that are not explicitly mentioned in this document, but are necessary to ensure a faultless room layout, installation and professional operation must be offered by the bidder (except for parts that are explicitly excluded from the tender).
1.5 | Standards and norms | The standards mentioned here may also be offered by equivalent standards as long as they cover the same requirements.
2 | Photovolatic Modules
2.1 | Photovolatic Modules | PV modules with crystalline technology. Output per module min. 400 Wp. or higher to reach capacity of 38,4 Wp. 2x Cable 1 x 4 mm² , min. 900mm lenght (alternatively with extension cable) The 2 cables must be firmly mounted to the panel. One cable must have a female connector and the other a male connector, incl. MC 4 plugs each, IP 67 according to the module and cable. Certification for wind load up to minimum 2400 Pa Solar cells are embedded in an EVA (ethylene vinyl acetate) layer, anti-reflective coating, front cover made of specially tempered, highly transparent glass. Framed with aluminium profile (anodised). Maximum NOCT 45°C.
2.2 | Certifications and standards | The module complies with the following certifications: - IEC 61 215 : Terrestrial photovoltaic (PV) modules - Type qualification and type approval. - IEC 61 730 : Photovoltaic (PV) modules - safety qualification The tests are carried out by recognised testing laboratories according to ISO/IEC 17025. The manufacturer of the solar modules can prove by a suitable certificate that a permanent quality control and assurance of the production processes takes place in his factory. It must be proven that the standards according to IEC 61215 and IEC 61730 are also adhered to in ongoing production. The certificate itself is issued by an accredited testing institute. The normative requirements IEC 60891 ; IEC 60904 ; IEC 61345 ; IEC 61701; IEC 61721; EN 50380 are fulfilled. CE Declaration of Conformity by the manufacturer is available. A confirmation by a conformity assessment body according to ISO/IEC 17021 is available. CE marking of the solar modules is available. The solar modules are marked accordingly. Weatherproof junction box on the back of the module. The junction box must comply with at least IP 65 and the DIN VDE 0126-5 standard. The cabling between the modules with connectors complies with the EN 50521 standard.
2.3 | Delivery | The modules must be packed on pallets for safe onforwarding to the final destination in Ukraine. Wooden boxes, cardboard or equivalent is suitable. IEC 62759-1 shall be observed with regard to the delivery/shipping of the modules. Flash data for each module must be provided as a digital file.
2.3 | Manufacturer Warranty | Linear performance guarantee for 25 years with maximum degradation coefficient of -0.5%/year Product guarantee for at least 10 years
2.4 | Please specify: | Brand name, model, type
Area of the cells (LxW) in mm
Dimensions of the module (LxWxD) in mm Cable length + and Cable length -
Weight of module in kg
Maximum power (Pmax) W
Maximum voltage ( Vmax) V
Maximum current ( Ipmax) A
Maximum reverse current IR [A]
Short-circuit current (Isc) A
Open circuit voltage ( Voc) V
Temperature coefficient for current A/°C
Temperature coefficient for voltage V/°C
Temperature coefficient for power %/°C
Nominal cell operating temperature ( NOCT)
Maximum system voltage ( Vsmax )
Operating temperature ( Min- Max ) °C
Ambient temperature ( Min - Max ) °C
Current-voltage characteristics at 25°C and other temperatures and irradiation
2.5 | Please enclose with quotation: | Data sheet
Test certificates according to IEC 61215 and IEC 61730
Certificates according to ISO/IEC 17025
Accreditation of the test centre/institute or test centres (IEC 61215, IEC 61730 and ISO/IEC 17025) according to EN 45011 - 45013
CE declaration of conformity of the manufacturer
Confirmation that upon delivery of the modules, the flasher protocols showing the rated power of all delivered modules are presented and handed over.
Declaration or explicit confirmation regarding the replacement of the modules according to item 2.3.
Explanations on packaging and handling of the solar modules with reference to IEC 62759-1
2.6 | EL measurements | The results and images of the flash tests and electroluminescence measurements issued to the serial numbers of the panels shall be submitted. All documents and technical documentation submitted must be legible and easily recognisable.
3 | Structure
3.1 | Structure | The substructure made of aluminium or steel must support the modules without bolting it to the roof. The structure needs to be installed on a flatroof top. It needs to withstand the local weather conditions. It must be sufficiently protected against corrosion. Angle of inclination: 30°. Special anti-theft bolts and nuts to match the modules. Lightning protection and earthing. The substructure must be contructed in such mannor, that every typ of balast can be used and not that any specialized ballast type is needed. The ballast material does not have to be deliverred by the bidder. The needed ballast should be precisely specified by the bidder so that it can be purcahsed by the final recipient.
3.2 | Manufacturer Warranty | min. 10 years
3.3 | Please specify: | Brand name, model, type
Data sheet
Detailed description of the anti-theft screws and nuts
Technical description of the substructure
Description of the lightning protection
3.4 | In case of order, to be provided before delivery: | Sectional drawings of the profiles and elevations
Detailed drawings of fixings (interfaces, connections)
Assembly instructions in English or Ukrainian
4 | Inverter
| One Inverter | The following functions are fulfilled: - enables supply of consumers with 230 V AC - 3 phase system requested - high voltage system recomended - charges the battery with an integrated MPPT charge controller. - simultaneously allows connection to a generator or power grid - U-I generator diagnosis - Protective conductor monitoring
| Capacity of one inverter | Continuous power max. 40 kVA each inverter System voltage 48 V Output voltage 230 V AC +/- 5% Output frequency 50/60 Hz Pure sine wave voltage Integrated 2 MPP tracker each iverter, multi-stage charging technology MPP voltage range up to 1200 V starting voltage up to 220 V nominal voltage range has to specified in the offer, a range is not specified
| Handling | Graphic LCD display or or simply connect it to a standard mobile device Menu-guided operation Serial interface RS-232, PC connection via USB, WIFI Incl. PC software
| Power protection | Overcharge protection Reverse polarity protection of modules, for battery via fuses Deep discharge protection Short-circuit protection of load and module Reverse polarity protection via internal fuses Reverse current protection at night Overtemperature and overload protection Audible alarm PE connection
| Certifications and standards | It must comply with the following standards: EN-IEC 60335-1, EN-IEC 60335-2-29, EN-IEC 62109-1, EN 55014-1, EN 55014-2, EN-IEC 61000-3-2, IEC 61000-6-1, IEC 61000-6-2, IEC 61000-6-3. Manufactured according to ISO 9001 and ISO 14001. CE compliant
| Manufacturer Warranty | min. 5 years
| Please specify: | Brand name, model, type
Data sheet
5 | Battery
| Lithium-ion-battery 28-32 kW | 3,000 cycles @50% DoD, 20°C / 1,500 cycles @80% DoD, 20°C Proof of conformity to IEC 60896-21/22 and IEC 61427 is required. Service life according to EUROBAT min. 12 years at 20°C Standards and regulations for installation: DIN EN 50272-2 (safety regulations for battery rooms) The battery must be supplied with its rack certified by the manufacturer. Proof of quality assurance system according to ISO 9001 / ISO 14001 ISO 45001 occupational health and safety or equivalent certification Fully insulated, corrosion-free lead terminal All pole penetrations must ensure complete electrolyte and gas tightness even when positive plate is growing Fully insulated copper connectors and screw heads Interconnection lead poles with torque 20 - 22 Nm Environmentally friendly, min. 98 % recyclable Energy efficiency > 80% Ampere-hour efficiency > 90% Self-discharge less than 2-3%/month at 20°C No memory effect Sufficiently large containers for electrolyte circulation Each battery is labelled with at least the following data: Manufacturer, type, model number, nominal voltage in V, nominal capacity in Ah, month and year of commissioning. Each cell must have a factory serial number
Energy capacity 28-32 KW Usable capacity 28 – 32 KW Peak output power min. 15-20KW/60s Battery type LiFePO4 Protection class IP20 Working temperature min. -5°C to 50°C Permissible humidity min. 5% to 95% Cooling Natural IEC62619 certificate IEC60730 VDE2510-50 CE marking UL1973 UL 9540A
| Charge regulator | Charge controller with MPPT technology. Maximum self-consumption 1 W. Complies with EN 62109-1. Electrical efficiency >90% (at 5 to 120% nominal power). Inverter has an integrated data logger (data storage on MMC/SD card or similar) Possibility to connect a remote control / remote monitoring is available Power supply for consumers (AC/DC) or battery charging via solar system or diesel generators (230 VAC) is possible Input voltage 230 V Protection class IP40
Supported battery types: Li-Ion, FLA, VRLA Charge control: IUoU with automatic full and equalisation charging Protection of the battery against deep discharge, (current-dependent final discharge voltage) Protection of the battery against overcharging Regular equalisation charge (e.g. regular increase of the final charge voltage) Display of switch-off due to deep discharge and other reasons Battery voltage display (e.g. via LED) External battery temperature sensor included in the scope of delivery Low overvoltage with inductive and capacitive loads (please specify value) Permissibility of half-wave operation caused by power reduction with diode, e.g. hair dryer Compliance with EMC limits according to EN 50081 and EN 55014 ISO certification of the manufacturer is available
Protection functions: Short-circuit proof Overload protection Overtemperature protection Lightning and overvoltage protection AC side Compliance with other VDE/IEC regulations (contact protection etc.) Compliance with EMC limits (electromagnetic compatibility) according to EN 50081 and EN 55014 Radio interference suppression (VHF) Output power control of the feed-in inverter (item 1.3) via frequency for overcharge protection of the battery Other normative requirements IEC 62093 ;DIN EN 5178 ; are fulfilled CE declaration of conformity by the manufacturer is available. Confirmation by a conformity assessment body in accordance with ISO/IEC 17021 is available. CE marking of the battery-charging inverter is available. The battery charging inverters are marked accordingly. Communication point if necessary Control cable (e.g. LIYCY paired 2x2x0.25 or comparable type) if necessary
6 | Cable
| Solar cables | 1 x 6 mm² copper cable (Solar cable H 1Z2Z2-K) with double insulation for up to 1000V, type C2 (high flame resistance), AN3 (high UV resistance) Maximum permissible conductor temperature at least 90°C in continuous use. The standard EN 50618 is fulfilled. Needed for each plant: 300m blue, 300m red, 200m black. Solar DC wiring must be carried out in accordance with IEC 62930:2017.
| Please specify: | Cable type and size, calculated cable length and price per meter
| MC plugs | 96 pcs male + 96 pcs female for each plant MC4 plugs or equivalent
| Please specify: | Cable type and size, calculated cable length and price per meter
| AC Cables | 60m NYY-J AC cable for each plant, 5x25 mm² Copper The AC wiring must be carried out in accordance with NFC 15-100 and according to the technical specifications for the building.
| Please specify: | Cable type and size, calculated cable length and price per meter
| Empty conduits | 200m grounding cable NYY-J 5x25 mm² Copper
| Cable ties | UV-resistant cable ties in all necessary sizes and quantities.
| Accessories | All accessories for proper fastening of the cables under the modules for the entire installation.
7 | erased
8 | erased
9 | Documentation
| The following documentation, in English or Ukrainian, must be supplied in electronic form for all components of the system after the order has been placed: | Assembly instructions for the entire system. Overview for an installer on site, showing which components are connected to each other and how. This overview also refers to the corresponding installation instructions and assembly instructions for the individual components.
Circuit document
Description of the components
Wiring diagrams
Assembly instructions, installation instructions
Commissioning instructions
Operating instructions
Maintenance instructions
Error analysis and troubleshooting suggestions in the event of a malfunction
10 | Delivery
| Delivery | All material must be delivered DDP different German places latest 12 weeks after order Each plant must be packed and marked singlely, always 2 plants needs to be deliverred to 1 destination. Expected destinations for deliveries are bad Urach, Bocholt, Erzhausen, Göttingen, Greifswald, Hürth, Montabaur, Pullach, Rudolstadt, Wolfrathshausen, Zwickau this destinations might change. Detailled addresses follows by giz with the order (2 plants each destination in Germany).
| Customs status | All goods must be EU Community goods or goods imported entirely into the EU. The bidder is responsible for import customs clearance into the EU, including all costs, duties and fees.
| Please specify: | Dimensions (LxWxH), weight (kg) incl. packaging for land shipment.
11 | erased
12 | Warranty
| min. 2 years | On the entire system and installation. Fully according to GIZ General Purchase Conditions (GPC) 2023. The claims arising from the product and system warranties apply in addition to the claims for defects in accordance with GIZ GPC 2023. For individual components, longer warranty periods apply if described.
| Guarantee assignment declarations | All manufactuer warranties must be assigned to GIZ and project partners by declaration. This declaration must be signed and stamped by each manufacturer.